## Sheet1
MODEL FOR STEAM COST AND SAVINGS USING ACS CERAMIC INSULATION COATING & PLANT EFFICIENCY INPUT
OVERVIEW OF CIC INSULATION WHEN APPLIED TO CONTINUOUS COOKERS
Energy Savings - The CIC insulation will reduce radiant & convective losses from a cooker shell. Depending on cooker ambient conditions, the energy losses (radiant & convective) will be reduced by 25% to 38%.
Calculation Technique - Previously, a reference cooker was set-up and tested (indoors) to determine the before and after heat losses (Heat was determined by measuring condensate.). The heat losses are a small portion of the total energy consumed, so this test is very difficult to repeat. For other cookers, we recommend modeling the reference cooker, rather than direct measurement of heat. This spreadsheet allows the user to predicted their cooker's conditions, based on the reference cooker. Simply enter your operating variables for your candidate cooker. Energy losses will be adjusted for differences from the reference cooker: surface area, cook temperature, ambient temperature, and steam & condensate heat content. Energy savings will be predicted.
Note - This spreadsheet assumes that the steam supply will be saturated, not superheated.
MODELING YOUR COOKER/CALCUATING YOUR SAVINGS
GUIDE TO COLOR-CODING OF CELLS & INPUT/OUTPUT VALUES:
Enter the operating variables for your cooker in these input cells, constants were entered in red
Variable "markers" (to the right of the input cells) and an explanation of the inputs required
Key output values (Important: do not change)
Data for reference cooker: calculations in black. Measured data in red
| COOKER OPERATING CONDITIONS | Units | Candidate Cooker | Reference Cooker |  |  | DESCRIPTION OF THE VARIABLES AND EXPLANATION OF THE CALCULATED VALUES
| Length of cooking season - total annual cooker operation | (days/yr) | 100 | n/a |  | 1 | Cooking Season Length in Days.
| Time cooker is hot each day - including warm-up & stand-by | (hrs/dys) | 24 | n/a |  | 2 | Cooker Heating Period each Day - this includes warm-up and stand-by time per Del Monte.
| Cooking temperature (internal cooker temperature) | (deg F) | 262 | 262 |  | 3 | Cooker Temperature - this is the cooking temperature for the food products
| Cook room temperature (ambient air temperature at cooker) | (deg F) | 80 | 65 |  | 4 | Ambient air temperature in the cook room
| Cook temp. differential for heat loss (interior minus exterior) | (deg F) | 182 | 197 |  |  | The amount of heat loss is linear with temperature differential. So, this comparison of temperature differentials will allow us to predict heat loss, based on the reference cooker
| COOKER GEOMETRY | Units | Candidate Cooker | Reference Cooker
| Cooker diameter | (ft) | 10 | 5 |  | 5 | Cooker Diameter - determines surface area heat loss and savings, pluse CIC insulation cost.
| Cooker length | (ft) | 40 | 30 |  | 6 | Cooker Length - determines surface area heat loss and savings, plus CIC insulation cost.
| Surface area: of cylindrical shell | (sq ft) | 1256.6371 | 471.2389
| Surface area: of heads | (sq ft) | 78.5398 | 19.635
| Surface area: total | (sq ft) | 1335.1769 | 490.8739 |  |  | The amount of heat loss is linear with surface area. So, this comparison of surface areas will allow us to predict heat loss, based on the reference cooker
| STEAM & CONDENSATE CONDITIONS INSIDE THE COOKER | Units | Candidate Cooker | Reference Cooker
| Steam pressure in the steam supply header | (psig) | 150 | 150 |  | 7 | The steam pressure in the supply header is the best indicator of the heat delivered into the cooker by the steam. Note: This is greater than the pressure inside the cooker.
| Heat content: steam entering the cooker (steam header conditions) | (btu/lb) | 1196.1406 | 1196 |  |  | The unit amount of heat contained in the steam as it enters the cooker from the supply header. Although the cooker is at a lower pressure, the heat from supply header conditions is still present in the form of some minor, short-term superheating. This value automatically comes from a steam table.
| Heat content: condensate leaving cooker | (btu/lb) | 230 | 230 |  |  | The unit amount of heat contained in the condensate as it leaves the cooker (prior to external flashing)
| Heat released by steam as it turns into condensate | (btu/lb) | 966.1406 | 966 |  |  | The unit amount of heat released by the steam before it leaves the cooker as condensate. Based on this comparison of the available heat, the amount of steam (lb/hr) required by the cooker will vary slightly, even if the heat load is identical.
| UNINSULATED COOKER HEAT LOSS (radiant & convective only) | Units | Candidate Cooker | Reference Cooker
| Ratio of temp differential: candidate cooker vs reference cooker | (count) | 0.92386 | n/a |  |  | The amount of heat loss is linear with temperature differential. So, this ratio of temperature differentials is one of two key factors for predicting heat loss, based on the reference cooker
| Ratio of surface area: candidate cooker vs reference cooker | (count) | 2.72 | n/a |  |  | The amount of heat loss is linear with surface area. So, this ratio of surface areas is one of two key factors for predict heat loss, based on the reference cooker
| Ratio of heat loss: candidate cooker vs reference cooker | (count) | 2.5129 | n/a |  |  | This factor incorporates all the changes in differential temperatures and surface areas between the candidate cooker and the reference cooker. It is the ratio between the the heat losses of the two cookers.
| Heat Loss - Total | (btu/hr) | 606863.7563 | 241500 |  |  | The heat loss is calculated for the uninsulated candidate cooker, based on a comparison with the reference cooker
| Steam used (and condensate generated) by the total heat loss | (lb/hr) | 628.132 | 250 |  |  | The steam use is calculated for the uninsulated candidate cooker, based on the heat relased by each pound of steam in the candidate cooker.
| INSULATION PERFORMANCE | Units | Candidate Cooker | Reference Cooker
| Percent reduction in heat loss after application of CIC insulation | (pct) | 25% | n/a |  | 8 | Energy Savings - Based on test data for rotary sterilizers, JBT Food Tech projects that the reduction in heat losses will be 25% (indoor) or 38% (outdoor). Del Monte's field test comparison of coated vs uncoated cookers indicated 25% savings, for an indoor installation. To be clear, this refers to the radiant and convetive heat losses from the surface of the steel vessel.
| INSULATED COOKER HEAT LOSS (radiant & convective only) | Units | Candidate Cooker | Reference Cooker
| Heat Loss - Total | (btu/hr) | 455147.8173 | n/a |  |  | The heat loss is calculated for the insulated candidate cooker, based on uninsulated cooker and insulation performance
| Steam used (and condensate generated) by the total heat loss | (lb/hr) | 471.099 | n/a |  |  | The steam used is calculated for the insulated candidate cooker, based on uninsulated cooker and insulation performance
| BOILER OPERATING CONDITIONS | Units | Pre-Insulation | Post- Insulation | Savings
| Temperature of the make-up water added to the Deaerator | (btu/lb) | 90 | 90 |  | 9 | Typically, make-up water enters the boiler room at ground water temperatures. However, it is often pre-heated with waste heat prior to entering the deaerator. In this cell, enter the temperature of the make-up water entering the deaerator.
| Heat content of make-up water added to the Deaerator | (btu/lb) | 58 | 58
| Heat content of the steam produced by the boiler | (btu/lb) | 1196.1406 | 1196.1406
| Heat added to make-up water to convert it into steam | (btu/lb) | 1138.1406 | 1138.1406 |  |  | This is the amount of heat that must be added to make-up water to convert one pound of it into steam. It is calculated by subtracting the enthalpy of the water from the enthalpy of the steam.
| Steam consumed by the cooker's radiant & convective losses | (lb/hr) | 628.132 | 471.099 | 157.033 |  | The amount of steam required by the cooker was calculated above.
| Heat added to the steam which is wasted by the cooker's losses | (btu/hr) | 714902.4529 | 536176.8397 | 178725.6132 |  | This is the hourly amount of heat added to the water to convert it into steam. It may be confusing that this amount of heat is greater than the amount of heat used by the cooker. This is because some of the steam's heat is wasted at the cooker because of the heat remaining in the condensate when it leaves the cooker.
| Boiler + Economizer efficiency (heat output ÷ heat input) | (pct) | 83% | 83% |  | 10 | Steam Plant Efficiency - specifies the relationship between steam output and required fuel input. If efficiency is not known, use one of these approximate figures: - Watertube boiler without feedwater economizer: 78.0% - Watertube boiler with feedwater economizer: 83.0% - Firetube boiler without feedwater economizer: 82.0% - Firetube boiler with feedwater economizer: 85.0%
| Boiler fuel consumed to make steam for cooker's losses | (btu/hr) | 861328.2565 | 645996.1924 | 215332.0641 |  | The boiler's heat input (fuel) is greater than the boiler's heat output (steam) because the boiler is less than 100% efficient.
| Unit cost of boiler fuel | ($/mmbtu) | 5.5 | 5.5 |  | 11 | Cost of fuel - subject to current + long term cost over 10 year forecasted lifespan of insulation.
| Fuel cost to "feed" the cooker's radiant & convective losses | ($/hr) | 4.7373 | 3.553 | 1.1843
SAVINGS CALCULATIONS
| Daily Operation - number of hours the cooker is hot | (hrs/day) | 24
| Annual Operation - number of days the cooker is hot | (days/yr) | 100
| Annual Operation - number of hours the cooker is hot | (hours/yr) | 2400
| Annual Steam Savings | (lb/yr) | 376879.1741
| Annual Heat Savings | (mmbtu/yr) | 516.797
| Annual Gas Savings | (therm/yr) | 5167.9695
| Annual Gas Savings | ($/yr) | 2842.3832
COST ESTIMATE FOR INSULATION OF A CONTINUOUS COOKER
MATERIAL COST
| Cooker length | (ft) | 40
| Cooker diameter | (ft) | 10
| Cooker's total surface area | (sq. ft.) | 1334.5
| Coverage factor for one 20 mil coating | (sq ft/gal) | 50 |  |  | 12 | Coverage factor for a single 20 mil coating
| Number of layers of coats for this project/proposal | (count) | 4 |  |  | 13 | Number of layers that will be applied in this project
| Safety factor for coverage calculation | (pct) | 15% |  |  | 14
| Quantity of CIC required to insulate the cooker | (gal) | 122.774
| Unit cost for CIC insulation material | ($/gal) | 50 |  |  | 15 | Unit cost that the customer will pay, including freight and tax
| Total cost for CIC insulation material | ($/gal) | 6138.7
LABOR COST
| Unit cost for application labor | ($/hr) | 50 |  |  | 16 | Wage rate for one applicator
| Unit cost for cleaning & preparation by plant staff | ($/hr) | 45 |  |  | 17 | Wage rate for one plant employee to do surface cleaning and preparation
| Man-Hours required for labor to apply the specified number of coats | (hours) | 8 |  |  | 18
| Man-Hours required for plant staff to clean & prepare the equipment | (hours) | 16 |  |  | 19
| Labor cost: application of coating by labor | ($) | 400
| Labor cost: cleaning & preparation by plant staff | ($) | 720
| Labor cost: total (application + cleaning & prep) | ($) | 1120
TOTAL COST
| Total Application Cost: material + labor | ($) | 7258.7 |  |  |  | Total application cost, prior to receipt of utility incentive payment
UTILITY REBATE
ENERGY SAVINGS DATA REQUIRED FOR DETERMINATION OF INCENTIVE PAYMENT
| Annual Operation - number of hours the cooker is hot | (hours/yr) | 2400
| Energy costs resulting from uninsulated heat losses: hourly | ($/hr) | 4.7373
| Energy costs resulting from uninsulated heat losses: annual | ($/yr) | 11369.533
| Reduction in heat losses (25% to 38%) | (pct) | 25%
| Energy savings in $$: annual | ($/yr) | 2842.3832
| Energy savings in Therms: annual | (therms/yr) | 5167.9695
PG&E ENERGY INCENTIVE PROGRAM
| PG&E incentive for CIC insulation, based on energy savings | ($/therm) | 0 |  |  | 20 | PG&E's incentive payment factor: incentive dollars per therm saved annually
| Incentive payment available for this project, if a PG&E customer | ($) | 0
SEMPRA ENERGY INCENTIVE PROGRAM
| Sempra incentive for CIC insulation, based on energy savings | ($/therm) | 1 |  |  | 21 | Sempra's incentive payment factor: incentive dollars per therm saved annually
| Incentive payment for this project, if PG&E or Sempra customer | ($) | 5167.9695
INCENTIVE PAYMENT AVAILABLE FOR THIS PROJECT, FROM THE APPLICABLE UTILITY
| Estimated rebate available for this project | ($) | 5167.9695 |  |  | 22 | Enter the rebate (from the rows above) for your particular utility.
INVESTMENT ANALYSIS
SIMPLE PAYBACK
| Total application costs for CIC Insulation (material + labor) | ($) | 7258.7
| Estimated annual energy savings | ($/yr) | 2842.3832
| Energy incentive payment (rebate amount) from the utility | ($) | 5167.9695
| Net application cost with savings = 1st yr. cost-rebate | ($) | -751.6528
| Simple payback period in days to cover application cost | Days | -26.4445 |  |  |  | Seasons required for simple payback of net investment. Note: if net application cost is negative, the payback period will be zero years.
NET PRESENT VALUE = PRESENT VALUE OF SUM OF MULTIPLE ANNUAL PAYMENTS (savings)
| Cost/Value of Capital (Industry) | (pct) | 5% |  |  | 23 | Enter the interest rate for capital cost (discount rate over the 10-year period)
| Net Present Value from: Cost, Yearly savings @ 10 year life | ($) | 19956.9581
YEARLY SAVINGS FOR ABOVE CALCULATION OF NET PRESENT VALUE
| Savings: Year 1 | ($/yr) | 751.6528
| Savings: Year 2 | ($/yr) | 2842.3832
| Savings: Year 3 | ($/yr) | 2842.3832
| Savings: Year 4 | ($/yr) | 2842.3832
| Savings: Year 5 | ($/yr) | 2842.3832
| Savings: Year 6 | ($/yr) | 2842.3832
| Savings: Year 7 | ($/yr) | 2842.3832
| Savings: Year 8 | ($/yr) | 2842.3832
| Savings: Year 9 | ($/yr) | 2842.3832
| Savings: Year 10 | ($/yr) | 2842.3832

## Steam Table (hidden)
PRESS | ENTHALPY | Next Higher Pressure
STEAM
(psig) | (btu/lb)
-14.6037 | 1075.6292 | -14.5999
-14.5999 | 1076.068 | -14.596
-14.596 | 1076.5066 | -14.592
-14.592 | 1076.9452 | -14.5878
-14.5878 | 1077.3837 | -14.5834
-14.5834 | 1077.8221 | -14.5789
-14.5789 | 1078.2604 | -14.5743
-14.5743 | 1078.6985 | -14.5694
-14.5694 | 1079.1366 | -14.5645
-14.5645 | 1079.5745 | -14.5593
-14.5593 | 1080.0124 | -14.554
-14.554 | 1080.4501 | -14.5484
-14.5484 | 1080.8877 | -14.5427
-14.5427 | 1081.3252 | -14.5368
-14.5368 | 1081.7625 | -14.5307
-14.5307 | 1082.1998 | -14.5244
-14.5244 | 1082.6369 | -14.5179
-14.5179 | 1083.0739 | -14.5111
-14.5111 | 1083.5107 | -14.5042
-14.5042 | 1083.9475 | -14.497
-14.497 | 1084.384 | -14.4895
-14.4895 | 1084.8205 | -14.4819
-14.4819 | 1085.2568 | -14.4739
-14.4739 | 1085.693 | -14.4658
-14.4658 | 1086.129 | -14.4573
-14.4573 | 1086.5649 | -14.4486
-14.4486 | 1087.0007 | -14.4396
-14.4396 | 1087.4363 | -14.4303
-14.4303 | 1087.8717 | -14.4208
-14.4208 | 1088.307 | -14.4109
-14.4109 | 1088.7422 | -14.4007
-14.4007 | 1089.1771 | -14.3902
-14.3902 | 1089.612 | -14.3794
-14.3794 | 1090.0466 | -14.3682
-14.3682 | 1090.4812 | -14.3567
-14.3567 | 1090.9155 | -14.3449
-14.3449 | 1091.3497 | -14.3327
-14.3327 | 1091.7837 | -14.3201
-14.3201 | 1092.2175 | -14.3071
-14.3071 | 1092.6512 | -14.2938
-14.2938 | 1093.0847 | -14.28
-14.28 | 1093.518 | -14.2659
-14.2659 | 1093.9511 | -14.2513
-14.2513 | 1094.3841 | -14.2363
-14.2363 | 1094.8169 | -14.2208
-14.2208 | 1095.2495 | -14.2049
-14.2049 | 1095.6819 | -14.1886
-14.1886 | 1096.1141 | -14.1717
-14.1717 | 1096.5461 | -14.1544
-14.1544 | 1096.9779 | -14.1366
-14.1366 | 1097.4096 | -14.1183
-14.1183 | 1097.841 | -14.0994
-14.0994 | 1098.2722 | -14.0801
-14.0801 | 1098.7032 | -14.0602
-14.0602 | 1099.1341 | -14.0397
-14.0397 | 1099.5647 | -14.0186
-14.0186 | 1099.9951 | -13.997
-13.997 | 1100.4253 | -13.9748
-13.9748 | 1100.8552 | -13.9519
-13.9519 | 1101.285 | -13.9285
-13.9285 | 1101.7145 | -13.9044
-13.9044 | 1102.1438 | -13.8796
-13.8796 | 1102.5729 | -13.8542
-13.8542 | 1103.0018 | -13.8281
-13.8281 | 1103.4304 | -13.8013
-13.8013 | 1103.8588 | -13.7738
-13.7738 | 1104.2869 | -13.7456
-13.7456 | 1104.7149 | -13.7166
-13.7166 | 1105.1425 | -13.6868
-13.6868 | 1105.57 | -13.6563
-13.6563 | 1105.9971 | -13.625
-13.625 | 1106.4241 | -13.5928
-13.5928 | 1106.8508 | -13.5599
-13.5599 | 1107.2772 | -13.5261
-13.5261 | 1107.7034 | -13.4914
-13.4914 | 1108.1293 | -13.4559
-13.4559 | 1108.5549 | -13.4194
-13.4194 | 1108.9803 | -13.382
-13.382 | 1109.4054 | -13.3437
-13.3437 | 1109.8302 | -13.3045
-13.3045 | 1110.2548 | -13.2642
-13.2642 | 1110.6791 | -13.223
-13.223 | 1111.1031 | -13.1807
-13.1807 | 1111.5268 | -13.1374
-13.1374 | 1111.9502 | -13.093
-13.093 | 1112.3733 | -13.0476
-13.0476 | 1112.7962 | -13.0011
-13.0011 | 1113.2187 | -12.9534
-12.9534 | 1113.6409 | -12.9046
-12.9046 | 1114.0629 | -12.8546
-12.8546 | 1114.4845 | -12.8035
-12.8035 | 1114.9058 | -12.7511
-12.7511 | 1115.3268 | -12.6975
-12.6975 | 1115.7475 | -12.6426
-12.6426 | 1116.1679 | -12.5864
-12.5864 | 1116.5879 | -12.529
-12.529 | 1117.0076 | -12.4702
-12.4702 | 1117.427 | -12.41
-12.41 | 1117.846 | -12.3485
-12.3485 | 1118.2647 | -12.2855
-12.2855 | 1118.6831 | -12.2211
-12.2211 | 1119.1011 | -12.1553
-12.1553 | 1119.5187 | -12.0879
-12.0879 | 1119.936 | -12.0191
-12.0191 | 1120.353 | -11.9487
-11.9487 | 1120.7696 | -11.8767
-11.8767 | 1121.1858 | -11.8031
-11.8031 | 1121.6016 | -11.7279
-11.7279 | 1122.0171 | -11.651
-11.651 | 1122.4322 | -11.5725
-11.5725 | 1122.8469 | -11.4922
-11.4922 | 1123.2613 | -11.4102
-11.4102 | 1123.6752 | -11.3264
-11.3264 | 1124.0888 | -11.2408
-11.2408 | 1124.5019 | -11.1534
-11.1534 | 1124.9147 | -11.0641
-11.0641 | 1125.327 | -10.9729
-10.9729 | 1125.739 | -10.8797
-10.8797 | 1126.1505 | -10.7846
-10.7846 | 1126.5616 | -10.6875
-10.6875 | 1126.9723 | -10.5884
-10.5884 | 1127.3826 | -10.4871
-10.4871 | 1127.7924 | -10.3838
-10.3838 | 1128.2018 | -10.2784
-10.2784 | 1128.6108 | -10.1707
-10.1707 | 1129.0193 | -10.0609
-10.0609 | 1129.4273 | -9.9488
-9.9488 | 1129.835 | -9.8344
-9.8344 | 1130.2421 | -9.7177
-9.7177 | 1130.6488 | -9.5987
-9.5987 | 1131.055 | -9.4773
-9.4773 | 1131.4608 | -9.3534
-9.3534 | 1131.8661 | -9.2271
-9.2271 | 1132.2709 | -9.0982
-9.0982 | 1132.6752 | -8.9668
-8.9668 | 1133.0791 | -8.8328
-8.8328 | 1133.4824 | -8.6962
-8.6962 | 1133.8853 | -8.557
-8.557 | 1134.2876 | -8.415
-8.415 | 1134.6895 | -8.2702
-8.2702 | 1135.0908 | -8.1227
-8.1227 | 1135.4916 | -7.9723
-7.9723 | 1135.8919 | -7.8191
-7.8191 | 1136.2916 | -7.6629
-7.6629 | 1136.6909 | -7.5038
-7.5038 | 1137.0896 | -7.3416
-7.3416 | 1137.4877 | -7.1764
-7.1764 | 1137.8853 | -7.0081
-7.0081 | 1138.2824 | -6.8367
-6.8367 | 1138.6789 | -6.6621
-6.6621 | 1139.0748 | -6.4842
-6.4842 | 1139.4702 | -6.303
-6.303 | 1139.865 | -6.1185
-6.1185 | 1140.2592 | -5.9307
-5.9307 | 1140.6528 | -5.7394
-5.7394 | 1141.0459 | -5.5446
-5.5446 | 1141.4383 | -5.3463
-5.3463 | 1141.8302 | -5.1445
-5.1445 | 1142.2215 | -4.939
-4.939 | 1142.6121 | -4.7298
-4.7298 | 1143.0022 | -4.5169
-4.5169 | 1143.3916 | -4.3002
-4.3002 | 1143.7804 | -4.0797
-4.0797 | 1144.1685 | -3.8553
-3.8553 | 1144.5561 | -3.627
-3.627 | 1144.9429 | -3.3947
-3.3947 | 1145.3292 | -3.1584
-3.1584 | 1145.7148 | -2.9179
-2.9179 | 1146.0997 | -2.6733
-2.6733 | 1146.484 | -2.4245
-2.4245 | 1146.8676 | -2.1714
-2.1714 | 1147.2505 | -1.9141
-1.9141 | 1147.6327 | -1.6523
-1.6523 | 1148.0143 | -1.3861
-1.3861 | 1148.3952 | -1.1154
-1.1154 | 1148.7753 | -0.84016
-0.84016 | 1149.1548 | -0.56032
-0.56032 | 1149.5336 | -0.2758
-0.2758 | 1149.9116 | 0.013434
0.013434 | 1150.2889 | 0.30746
0.30746 | 1150.6655 | 0.60633
0.60633 | 1151.0414 | 0.91011
0.91011 | 1151.4165 | 1.2189
1.2189 | 1151.7909 | 1.5326
1.5326 | 1152.1645 | 1.8515
1.8515 | 1152.5374 | 2.1756
2.1756 | 1152.9095 | 2.5048
2.5048 | 1153.2809 | 2.8394
2.8394 | 1153.6515 | 3.1793
3.1793 | 1154.0212 | 3.5246
3.5246 | 1154.3903 | 3.8754
3.8754 | 1154.7585 | 4.2317
4.2317 | 1155.1259 | 4.5936
4.5936 | 1155.4925 | 4.9613
4.9613 | 1155.8583 | 5.3346
5.3346 | 1156.2233 | 5.7138
5.7138 | 1156.5875 | 6.0989
6.0989 | 1156.9508 | 6.49
6.49 | 1157.3133 | 6.887
6.887 | 1157.675 | 7.2902
7.2902 | 1158.0358 | 7.6995
7.6995 | 1158.3958 | 8.115
8.115 | 1158.7549 | 8.5369
8.5369 | 1159.1131 | 8.9651
8.9651 | 1159.4705 | 9.3998
9.3998 | 1159.827 | 9.8411
9.8411 | 1160.1826 | 10.2889
10.2889 | 1160.5373 | 10.7434
10.7434 | 1160.8912 | 11.2046
11.2046 | 1161.2441 | 11.6727
11.6727 | 1161.5961 | 12.1476
12.1476 | 1161.9472 | 12.6296
12.6296 | 1162.2974 | 13.1185
13.1185 | 1162.6466 | 13.6147
13.6147 | 1162.9949 | 14.118
14.118 | 1163.3423 | 14.6286
14.6286 | 1163.6888 | 15.1466
15.1466 | 1164.0342 | 15.672
15.672 | 1164.3788 | 16.2049
16.2049 | 1164.7223 | 16.7455
16.7455 | 1165.0649 | 17.2937
17.2937 | 1165.4065 | 17.8497
17.8497 | 1165.7471 | 18.4135
18.4135 | 1166.0868 | 18.9853
18.9853 | 1166.4254 | 19.565
19.565 | 1166.763 | 20.1529
20.1529 | 1167.0997 | 20.749
20.749 | 1167.4353 | 21.3533
21.3533 | 1167.7699 | 21.966
21.966 | 1168.1034 | 22.5871
22.5871 | 1168.4359 | 23.2167
23.2167 | 1168.7674 | 23.8549
23.8549 | 1169.0979 | 24.5018
24.5018 | 1169.4273 | 25.1575
25.1575 | 1169.7556 | 25.8221
25.8221 | 1170.0829 | 26.4957
26.4957 | 1170.4091 | 27.1782
27.1782 | 1170.7342 | 27.8699
27.8699 | 1171.0582 | 28.5709
28.5709 | 1171.3812 | 29.2811
29.2811 | 1171.703 | 30.0008
30.0008 | 1172.0238 | 30.73
30.73 | 1172.3434 | 31.4687
31.4687 | 1172.662 | 32.2172
32.2172 | 1172.9794 | 32.9754
32.9754 | 1173.2957 | 33.7435
33.7435 | 1173.6108 | 34.5215
34.5215 | 1173.9248 | 35.3096
35.3096 | 1174.2377 | 36.1079
36.1079 | 1174.5494 | 36.9164
36.9164 | 1174.86 | 37.7353
37.7353 | 1175.1694 | 38.5646
38.5646 | 1175.4776 | 39.4044
39.4044 | 1175.7846 | 40.2549
40.2549 | 1176.0905 | 41.1161
41.1161 | 1176.3952 | 41.9882
41.9882 | 1176.6987 | 42.8712
42.8712 | 1177.001 | 43.7652
43.7652 | 1177.3021 | 44.6704
44.6704 | 1177.602 | 45.5867
45.5867 | 1177.9006 | 46.5145
46.5145 | 1178.1981 | 47.4536
47.4536 | 1178.4943 | 48.4043
48.4043 | 1178.7892 | 49.3667
49.3667 | 1179.0829 | 50.3408
50.3408 | 1179.3754 | 51.3267
51.3267 | 1179.6667 | 52.3246
52.3246 | 1179.9566 | 53.3346
53.3346 | 1180.2453 | 54.3567
54.3567 | 1180.5327 | 55.391
55.391 | 1180.8189 | 56.4378
56.4378 | 1181.1037 | 57.497
57.497 | 1181.3873 | 58.5689
58.5689 | 1181.6696 | 59.6534
59.6534 | 1181.9506 | 60.7507
60.7507 | 1182.2302 | 61.861
61.861 | 1182.5086 | 62.9842
62.9842 | 1182.7856 | 64.1206
64.1206 | 1183.0613 | 65.2703
65.2703 | 1183.3356 | 66.4333
66.4333 | 1183.6087 | 67.6097
67.6097 | 1183.8803 | 68.7998
68.7998 | 1184.1506 | 70.0035
70.0035 | 1184.4196 | 71.221
71.221 | 1184.6872 | 72.4524
72.4524 | 1184.9534 | 73.6979
73.6979 | 1185.2183 | 74.9575
74.9575 | 1185.4817 | 76.2314
76.2314 | 1185.7438 | 77.5196
77.5196 | 1186.0045 | 78.8223
78.8223 | 1186.2638 | 80.1396
80.1396 | 1186.5216 | 81.4717
81.4717 | 1186.7781 | 82.8186
82.8186 | 1187.0331 | 84.1804
84.1804 | 1187.2867 | 85.5573
85.5573 | 1187.5389 | 86.9494
86.9494 | 1187.7896 | 88.3568
88.3568 | 1188.0388 | 89.7796
89.7796 | 1188.2867 | 91.218
91.218 | 1188.533 | 92.6721
92.6721 | 1188.7779 | 94.1419
94.1419 | 1189.0213 | 95.6277
95.6277 | 1189.2632 | 97.1294
97.1294 | 1189.5037 | 98.6474
98.6474 | 1189.7426 | 100.1816
100.1816 | 1189.9801 | 101.7322
101.7322 | 1190.216 | 103.2994
103.2994 | 1190.4504 | 104.8832
104.8832 | 1190.6833 | 106.4837
106.4837 | 1190.9147 | 108.1012
108.1012 | 1191.1445 | 109.7357
109.7357 | 1191.3728 | 111.3873
111.3873 | 1191.5996 | 113.0562
113.0562 | 1191.8248 | 114.7426
114.7426 | 1192.0484 | 116.4464
116.4464 | 1192.2704 | 118.1679
118.1679 | 1192.4909 | 119.9072
119.9072 | 1192.7098 | 121.6645
121.6645 | 1192.9271 | 123.4397
123.4397 | 1193.1428 | 125.2332
125.2332 | 1193.3569 | 127.0449
127.0449 | 1193.5694 | 128.8751
128.8751 | 1193.7802 | 130.7238
130.7238 | 1193.9894 | 132.5913
132.5913 | 1194.197 | 134.4776
134.4776 | 1194.403 | 136.3828
136.3828 | 1194.6073 | 138.3072
138.3072 | 1194.8099 | 140.2508
140.2508 | 1195.0108 | 142.2137
142.2137 | 1195.2101 | 144.1962
144.1962 | 1195.4078 | 146.1982
146.1982 | 1195.6037 | 148.2201
148.2201 | 1195.7979 | 150.2619
150.2619 | 1195.9904 | 152.3237
152.3237 | 1196.1812 | 154.4056
154.4056 | 1196.3703 | 156.5079
156.5079 | 1196.5576 | 158.6307
158.6307 | 1196.7433 | 160.774
160.774 | 1196.9271 | 162.9381
162.9381 | 1197.1092 | 165.123
165.123 | 1197.2896 | 167.329
167.329 | 1197.4682 | 169.5561
169.5561 | 1197.645 | 171.8044
171.8044 | 1197.82 | 174.0743
174.0743 | 1197.9932 | 176.3656
176.3656 | 1198.1647 | 178.6787
178.6787 | 1198.3343 | 181.0137
181.0137 | 1198.5021 | 183.3706
183.3706 | 1198.668 | 185.7497
185.7497 | 1198.8321 | 188.1511
188.1511 | 1198.9944 | 190.5749
190.5749 | 1199.1549 | 193.0213
193.0213 | 1199.3134 | 195.4904
195.4904 | 1199.4701 | 197.9823
197.9823 | 1199.6249 | 200.4973
200.4973 | 1199.7778 | 203.0354
203.0354 | 1199.9288 | 205.5968
205.5968 | 1200.0779 | 208.1816
208.1816 | 1200.2251 | 210.7901
210.7901 | 1200.3704 | 213.4223
213.4223 | 1200.5137 | 216.0784
216.0784 | 1200.6551 | 218.7585
218.7585 | 1200.7946 | 221.4628
221.4628 | 1200.932 | 224.1915
224.1915 | 1201.0675 | 226.9446
226.9446 | 1201.201 | 229.7224
229.7224 | 1201.3326 | 232.525
232.525 | 1201.4621 | 235.3525
235.3525 | 1201.5896 | 238.2051
238.2051 | 1201.7151 | 241.0829
241.0829 | 1201.8385 | 243.9862
243.9862 | 1201.9599 | 246.915
246.915 | 1202.0793 | 249.8695
249.8695 | 1202.1966 | 252.8498
252.8498 | 1202.3118 | 255.8562
255.8562 | 1202.425 | 258.8888
258.8888 | 1202.5361 | 261.9476
261.9476 | 1202.645 | 265.033
265.033 | 1202.7519 | 268.145
268.145 | 1202.8566 | 271.2837
271.2837 | 1202.9592 | 274.4495
274.4495 | 1203.0597 | 277.6423
277.6423 | 1203.158 | 280.8624
280.8624 | 1203.2541 | 284.1099
284.1099 | 1203.3481 | 287.385
287.385 | 1203.4399 | 290.6878
290.6878 | 1203.5295 | 294.0186
294.0186 | 1203.6169 | 297.3774
297.3774 | 1203.702 | 300.7644
300.7644 | 1203.785 | 304.1798
304.1798 | 1203.8657 | 307.6238
307.6238 | 1203.9441 | 311.0964
311.0964 | 1204.0203 | 314.5979
314.5979 | 1204.0942 | 318.1285
318.1285 | 1204.1658 | 321.6882
321.6882 | 1204.2352 | 325.2774
325.2774 | 1204.3022 | 328.896
328.896 | 1204.3669 | 332.5443
332.5443 | 1204.4293 | 336.2225
336.2225 | 1204.4893 | 339.9306
339.9306 | 1204.547 | 343.669
343.669 | 1204.6023 | 347.4377
347.4377 | 1204.6552 | 351.2369
351.2369 | 1204.7058 | 355.0668
355.0668 | 1204.7539 | 358.9276
358.9276 | 1204.7997 | 362.8194
362.8194 | 1204.843 | 366.7423
366.7423 | 1204.8838 | 370.6966
370.6966 | 1204.9222 | 374.6825
374.6825 | 1204.9582 | 378.7
378.7 | 1204.9917 | 382.7494
382.7494 | 1205.0226 | 386.8308
386.8308 | 1205.0511 | 390.9445
390.9445 | 1205.0771 | 395.0905
395.0905 | 1205.1005 | 399.269
399.269 | 1205.1214 | 403.4803
403.4803 | 1205.1397 | 407.7245
407.7245 | 1205.1555