2017 Pacific Northwest Power Supply Adequacy Assessment and State of the System Report

DRAFT – Version 4

1/3/2013

2017 
Pacific Northwest Power Supply Adequacy Assessment and
State of the System Report

Contents

Executive Summary	3

Summary	4

Pacific NW Resource Adequacy Standard	8

Previous Assessments	9

2017 Resource Adequacy Assessment	9

Other Adequacy Metrics	12

Dealing with Uncertainties	12

Reliance on Market Supply	14

Generating Resources Dispatch	16

Curtailment Statistics	19

Appendix A – Assumptions	29

Appendix B – 2017 Resources and Loads	32

Appendix C – Assuring Adequacy for a Resource Plan	46

# Executive Summary

In 2010, as a part of its Sixth Power Plan, the Northwest Power and Conservation Council reported that the region’s power supply was on the cusp of becoming inadequate by 2015. Based on an assessment prepared by the Resource Adequacy Forum, the plan noted that relying only on existing resources and targeted energy efficiency savings would result in a 5 percent likelihood of a shortfall, which is right at the limit the Council adopted in 2008. This result is consistent with the plan’s finding that energy efficiency could meet most but not all forecasted load growth.

In this updated assessment, the forum concludes that the likelihood of a shortfall in 2017 has increased to 6.6 percent. This means that the region will have to acquire additional resources in order to maintain an adequate power supply, a finding that supports acquisition actions currently being taken by regional utilities.

Between 2015 and 2017, regional electricity demands, net of planned energy efficiency savings, are expected to grow by about 300 average megawatts. Since the last assessment, 114 megawatts of new thermal capacity, about 1,200 megawatts of new wind capacity and about 250 megawatts of small hydro and hydro upgrades have been added to the analysis. Also, a Northwest utility has contracted to purchase 380 megawatts of capacity from an independent power producer, which shifts this in-region generation from the market supply to firm resource status. Meanwhile, availability of the winter California market is assumed to decrease from 3,200 to 1,700 megawatts, mainly due to the retirement of coastal water-cooled thermal power plants.

The majority of potential future problems are short-term capacity shortfalls. The most critical months are January and February and, to a lesser extent, August. This is a different result from the 2015 assessment, which indicated that August was the most critical month. The major reason for this shift is the use of an updated streamflow record, which contains 10 more years of historical flows, new irrigation withdrawal amounts and various updates to reservoir operations both in the U.S. and Canada. The net result yields a higher average streamflow in August, thus improving summer adequacy.

The forum analyzed two different approaches to lowering the likelihood of a shortfall in 2017 back down to the 5 percent limit.  Results show that adding 350 megawatts of additional dispatchable generation capacity or lowering the 2017 annual load by 300 average megawatts would bring the likelihood of a shortfall back down to the 5 percent limit. Demand response may also be a viable option but was not analyzed.

It should be noted that this assessment is not a substitute for a comprehensive resource acquisition plan. The optimal amount and mix of new resources needed to provide an adequate, efficient, economic and reliable regional power system is determined by the Council’s power plan. This assessment also does not fully reflect constraints and needs of individual utilities within the region. Thus, these results should be viewed as a conservatively lower bound on regional needs for new resource capacity.

# Summary

The Resource Adequacy Standard and What it Means

In 2008, the Northwest Power and Conservation Council adopted a regional power supply adequacy standard to “provide an early warning should resource development fail to keep pace with demand growth.” The standard, developed by the Northwest Resource Adequacy Forum, deems the power supply to be inadequate should the likelihood of curtailment five years in the future be higher than 5 percent. The forum uses probabilistic analysis to assess that likelihood, most often referred to as the loss of load probability.

The assessment only counts existing resources and those expected to be operational. It also includes targeted energy efficiency savings from the Council’s Sixth Power Plan. When the likelihood of curtailment exceeds the 5 percent limit, a separate analysis is made to quantify the minimum amount of new generation capacity or load reduction needed to bring the loss of load probability back down to 5 percent.

2017 Resource Adequacy Assessment

The last official adequacy assessment was adopted as part of the Sixth power plan. That assessment indicated the region’s power supply for 2015 was on the cusp of becoming inadequate -- the implied loss of load probability was 5 percent.

Between 2015 and 2017, the region’s electricity loads, net of planned energy efficiency savings, are expected to grow by about 300 average megawatts or about a 0.7 percent annual rate. Since the last assessment, 114 megawatts of new thermal capacity and about 1,200 megawatts of new wind capacity have been added along with about 250 megawatts of small hydro and hydro upgrades.  The recent acquisition of 380 megawatts of a regional independent power resource has been included and the in-region market supply has correspondingly decreased.

California is expected to retire a substantial amount of its coastal water-cooled thermal power plants. It is also uncertain whether two units at the San Onofre Nuclear Generating Station will be operational in 2017. As a result, the forum reduced its assumption for the availability of California winter on-peak market supply from 3,200 to 1,700 megawatts.

Taking all of these changes into account, the expected loss of load probability for the 2017 power supply is 6.6 percent, indicating an inadequate supply if no additional resources are acquired. Types of potential problems the region could face range from energy shortfalls that could last for several days to peak curtailments that last several hours. Results show that the majority of simulated shortfalls are four hours or less in duration and over 40 percent are two hours or less.

To minimize cost and risk, new resource additions should be tailored to specifically address the expected types of shortfalls, that is, peak-hour shortages. This suggests that capacity resources such as simple-cycle combustion turbines or demand response programs or winter-peaking energy efficiency measures should be considered. It should be noted again, however, that the scope of this assessment is only to provide a gauge of the relative adequacy of the power supply.  The determination of the quantity and mix of new resource capacity needed make the power supply adequate is left to more comprehensive integrated resource planning processes.

With that being said, the forum analyzed two different approaches to lowering the likelihood of a shortfall in 2017 back down to the 5 percent limit.  First it examined how much additional dispatchable generating capacity would be needed to reduce the likelihood to 5 percent and secondly, it examined how much of an annual load reduction would accomplish the same objective. The results show that adding 350 megawatts of new dispatchable generation capacity would lower the 6.6 percent likelihood down to 5 percent. The same level of adequacy can be achieved by lowering the 2017 annual load by 300 average megawatts. Demand response is another alternative but the forum did not examine how much would be needed.

The findings for 2017 are consistent with assessments made by regional utilities indicating a need for new resources. It is also consistent with the plan, which concluded that energy efficiency alone will not be sufficient to offset all future load growth. In aggregate, utility planned resources far exceed the 350 megawatt gap.

In the analysis for 2017, the most critical months are January and February and, to a lesser extent, August. This is a different result from the last official assessment, which indicated that August was the most critical month. The major reason for this shift is the use of an updated streamflow record.  The new record contains;

- 80 years of historical streamflow data (the old record had 70 years)

- New irrigation withdrawal amounts

- More current Canadian system operation (both for treaty and non-treaty storage)

- Updated operating requirements at Grand Coulee

- More accurate representation of the operation of Snake River Basin dams

- Other miscellaneous adjustments at various hydroelectric projects

These changes, in aggregate, result in an overall shift in streamflows across the months of the year.  In particular, the average August streamflow is expected to increase by about 10,000 cubic feet per second, which translates into about 650 megawatts of additional power for the regional system.

Dependence on the Market

The methodology used to assess the adequacy of the Northwest power supply assumes a certain amount of reliance on market power supplies, both from within the region and from California. A significant part of the Northwest market is made up of independent power producer resources. The full capability of these resources, about 3,450 megawatts, is assumed to be available for Northwest use during winter months. However, during summer months, due to competition with California utilities, the Northwest market availability for Northwest use is limited to 1,000 megawatts.

The California market is broken into on-peak and off-peak availabilities. The off-peak availability is assumed to be 3,000 megawatts year round. Energy from the off-peak market is purchased during light-load hours prior to periods of potential shortfalls and is often referred to as a purchase-ahead resource. The on-peak availability is assumed to be 1,700 megawatts during winter and not available at all during summer.

Northwest utilities routinely rely on market resources to maintain an adequate power supply.  The amount of market resources used depends on a number of conditions, with the biggest factors being stream flow levels, outages of utility-owned resources, and temperature-driven load variations. For 2017, assuming only existing resources and targeted energy efficiency, the analysis shows the region would purchase an average of 1,170 megawatt-months of market supplied energy in December representing about 18 percent of the total available energy (6,450 megawatts-months). In August the region is would purchase an average of 400 megawatt-months of market supplied energy or approximately 10 percent of the total available energy (4,000 megawatts-months).

However, averages can be misleading and a more important statistic is how much market supplied energy is needed during extreme events when the regional load-resource balance tightens. Ten percent of the time, market purchases would exceed 2,200 megawatt-months in December (34 percent of the total) and 820 megawatt-months in August (21 percent of the total). The full amount of market supplied energy would be needed in less than 1 percent of all hours.

Uncertainties

The forum’s analytical tools account for uncertainties in stream flows, wind generation, temperature-driven demand variations, and generating resource availability. However, there are additional uncertainties that are not explicitly modeled. Two of the more significant uncertainties are economic load growth and the availability of the California energy market. The expected 6.6 percent loss of load probability assumes the Council’s medium load forecast and 1,700 megawatts of expected California on-peak winter market supply.

To investigate the potential impacts of different combinations of economic load growth and California market availability, scenario analyses were performed. In the worst case, with high load growth and no California market, the loss of load probability would be 16.8 percent. The good news is that this scenario is very unlikely. In the best case, with low load growth and 3,200 megawatts of California market, the loss of load probability drops to 2.8 percent, well within the Council’s limit.

While the current assessment provides the best estimate for the probability of a power supply shortage, the loss of load probability could be larger or smaller depending on load and market conditions in 2017. And, because the uncertainty surrounding these particular variables is not well defined, it is difficult to develop a range of likely loss of load probability values. What is clear is that there is a relatively high chance that the region will need some level of new resource development by 2017 in order to maintain an adequate supply.

Future Assessments

The Resource Adequacy Forum will continue to annually assess the adequacy of the power supply. However, this task is becoming more difficult because the power supply has become more complex in recent years. The increase in variable generation resources, combined with changing patterns for electricity demand, is forcing utility planners and operators to more carefully assess what resources are needed in reserve to ensure that demand can be met minute to minute. The current adequacy assessment incorporates a certain amount of minute-to-minute reserves, but it is not certain that they will be sufficient. Regional planners are evaluating various methods to quantify and plan for these flexibility needs.

Another emerging concern is the lack of access for some utilities to market supplies due to insufficient transmission or other factors. For the current adequacy assessment, the Northwest region is split into two subsections and only the major East-West transmission lines are modeled. Similarly, only the major Canadian-US and Northwest-Southwest interties are modeled.  It may be necessary to divide the Northwest region into more subsections to better address the effects of transmission congestion on power supply adequacy.

Resource adequacy continues to be a concern in the Northwest. The forum’s results are consistent with regional utility integrated resource planning, which supports the need for additional capacity. The Council and forum will continue to improve methods used to assess the power supply adequacy.

# Pacific NW Resource Adequacy Standard

In December of 2011, the Northwest Power and Conservation Council adopted an adequacy standard for the regional power supply.  The standard, recommended by the Resource Adequacy Forum, provides an early warning should resource development and efficiency savings fail to keep pace with demand growth.

Power supply adequacy is assessed by using a probabilistic analysis to compute the likelihood of a supply shortfall five years into the future.  The analysis is based on a chronological hourly simulation of the region’s power supply over many different future combinations of stream flows, temperatures, wind generation and forced generator outages.  Only existing generating resources and those that are expected to be operational five years out are counted along with targeted energy efficiency savings.  The simulation also assumes a conservative amount of market resource availability, both within and outside of the region.

The power supply is deemed to be inadequate if the likelihood of a shortfall (referred to as the loss of load probability or LOLP) is greater than 5 percent.  In such cases, the Forum also estimates how much new dispatchable resource generating capacity is required to bring the system’s LOLP back down to 5 percent.  This standard, however, is not intended to provide a resource planning target because it assesses only one of the Council’s criteria for developing a power plan.  The Council must develop a plan that provides an adequate, efficient, economic and reliable power supply.  There is no guarantee that a power supply that satisfies the adequacy standard will also be the most economical or efficient.  Thus, the adequacy standard should be thought of as simply an early warning to test for sufficient resource development.

Use of Standby Resources

Standby resources are demand-side actions and small generating machines that are not explicitly modeled in the adequacy analysis. They are mainly composed of demand response measures, load curtailment agreements and small thermal resources.

Demand response measures, are expected to be used every year to help lower demand during peak hours of the day. These resources only have a capacity component and are not intended to provide extended energy relief. To the extent that these measures have been implemented, their contribution is already reflected in the Council’s load forecast. New demand response measures that have no operating history and are therefore not accounted for in the load forecast are classified as part of the set of standby resources.

Load curtailment actions and small generating resources that are contractually available to utilities help reduce peak hour load and may also provide some energy assistance. However, they are not intended to be used often. The energy and capacity capabilities of these non-modeled resources are aggregated along with the demand response measures mentioned above to define the total capability of standby resources. A post-processing algorithm uses these capabilities to adjust the simulated curtailment record and calculate the final LOLP.

Currently, the aggregate energy capability of standby resources, as we have defined them, is 83,000 megawatt-hours. The peaking capability of these resources varies by season, with a 660 megawatt capacity in winter and a 720 megawatt capacity in summer.

# Previous Assessments

The history of adequacy measures for the Pacific Northwest power supply dates back more than half a century. Although probabilistic methods to assess adequacy had been around for awhile, limited computer capability made it nearly impossible to use them. Thus, since about the turn of the century, deterministic measures were used. These measures simply counted up available resources and compared their aggregate energy availability to the forecasted energy load. The criterion for an adequate supply was (implied) that energy availability had to be greater than the expected annual energy demand. Because of the predominance of hydro power in the Northwest, the region was fuel short (energy) and machine rich (capacity) so the criterion focused only on energy. The annual energy and load assessments were published in the PNUCC Northwest Regional Forecast and in the BPA White Book.

There were some key assumptions in that calculation that should be emphasized. The first is that the Northwest was assumed to be an island and thus, no out-of-region market supplies were counted. And, at the time, no in-region market resources existed. The second is that critical hydro generation was used to assess the hydroelectric system’s energy availability. Critical hydro generation is the amount of energy produced when the region’s lowest historical streamflows are combined with reservoir storage operations to shape hydro generation to monthly loads. This sequence of low water conditions is referred to as the “critical period.” Critical hydro generation was intended to represent the amount of “firm” or “guaranteed” hydro generation. Critical period streamflows were used to assess the amount of firm hydro generation because of limited reservoir storage in the Northwest, where the total useable storage is only about 15 percent of the average annual runoff volume of water. If reservoir storage were greater, say at least equal to the average runoff volume, then “average” hydro conditions could be used to assess firm hydro generation.

But even early on it was generally accepted that the planning standard (energy availability must equal average load) was too conservative because Southwest market supplies are generally available during the Northwest’s peak winter season and the likelihood of a critical period repeat is very low (perhaps 1 or 2 percent). Building new resources to this strict standard would likely lead to a high cost power supply with thermal resources often being displaced by cheaper hydro generation. In order to reduce resource additions and keep costs down, an agreement was made between utilities and aluminum companies that made part of the aluminum load nonfirm in return for a cheaper rate. This effectively increased the amount of firm hydro generation. However, since then much of the aluminum load has gone away.

Nonetheless, even without the aluminum industry’s nonfirm contracts, planners understand that building to meet a slight “firm” deficit (as defined above) is actually more cost effective than planning to meet a balanced system. The problem is that no one really knew at that time how much of a deficit to plan to, in other words, where to draw the line to differentiate between an adequate power supply from an inadequate one. This was exacerbated in 1998 when the anticipated balance for the following year was nearing a 4,000 average megawatt deficit. The BPA administrator appealed to the Council to develop a more precise measure of adequacy. This invigorated discussions of probabilistic measures and lead the Council to develop the GENESYS model, which has the capability of assessing the likelihood of potential future shortfalls. The first assessment, made for 2003, yielded a 24 percent loss of load probability -- much higher than the anticipated maximum of 5 percent. Then the 2001 energy crisis hit with a non-functioning California market and the second driest conditions on record.

Table 1- Adequacy Milestones

| Year | Milestone |
| --- | --- |
| 1998 | Large load/resource balance deficit concern |
| 1999 | Ad-hoc committee recommends using LOLP, GENESYS created |
| 2000 | First assessment yields 24 percent LOLP -- much higher than 5 percent standard |
| 2001 | West Coast energy crisis |
| 2005 | Resource Adequacy Forum created |
| 2007 | Unofficial assessment for 2013 indicates an adequate supply |
| 2008 | Council adopts first adequacy standard, translates LOLP to deterministic measures |
| 2009-10 | Adequacy methodology is peer reviewed |
| 2010 | Council’s 6th plan implies a 5 percent LOLP for 2015 |
| 2011 | Council revises its adequacy standard, uses only LOLP |
| 2012 | Assessment for 2017 shows an inadequate supply with LOLP at 6.6 percent |

Table 1 illustrates the evolving nature of the effort to better quantify power supply adequacy. Over the seven years since the Adequacy Forum was established, the methodology and associated assumptions have changes significantly, making it difficult to compare annual assessments. And, while this evolution is likely to continue, the Forum now believes that the current standard and assumptions will be fairly stable. This year’s assessment for the 2017 operating year is the first assessment with the revised standard and assumptions from 2011. The Forum hopes that this year’s assessment along with future assessments will create a history of adequacy evaluations that can be used to record trends over time.

# 2017 Resource Adequacy Assessment

In spite of the changing nature of adequacy assessments over this past decade, we can infer from studies done for the 2015 operating year that the power supply was estimated to be on the cusp of inadequacy. That assessment, reported in the Council’s 6th Power Plan, indicated that the summer sustained peak reserve margin was right at the limit set by the first standard adopted by the Council in 2008. That analysis implies that the LOLP for 2015 would have been right at 5 percent, which is the current standard’s threshold.

Between 2015 and 2017, the region’s electricity loads, net of planned energy efficiency savings, are expected to grow by about 300 average megawatts or about a 0.7 percent annual rate. Since the last assessment, 114 megawatts of new thermal capacity and about 1,200 megawatts of new wind capacity have been added along with about 250 megawatts of small hydro and hydro upgrades.  The recent acquisition of 380 megawatts of a regional independent power resource has been included and the in-region market supply has correspondingly decreased.

California is expected to retire a substantial amount of its coastal water-cooled thermal power plants. It is also uncertain whether two units at the San Onofre Nuclear Generating Station will be operational in 2017. As a result, the forum reduced its assumption for the availability of California winter on-peak market supply from 3,200 to 1,700 megawatts.

Taking all of these changes into account, the expected loss of load probability for the 2017 power supply is 6.6 percent, indicating an inadequate supply if no additional resources are acquired. Types of potential problems the region could face range from energy shortfalls that could last for several days to peak curtailments that last several hours. Results show that the majority of simulated shortfalls are four hours or less in duration and over 40 percent are two hours or less.

The 6.6% LOLP value indicates that the power supply is inadequate, in other words, the likelihood of a serious shortfall is greater than the region’s tolerance for such events.  This value is driven by single hour shortfalls in August.  Assessing the LOLP based solely on energy results in a value of 1.4 percent.  Figures 1 and 2 show the curtailment probability curves for total annual energy and single hour shortfalls.

Figure 1 - Annual Curtailment Energy Probability Curve

Figure 2 - Max Peak Curtailment Probability Curve

Figure 3 - Monthly LOLP

Figure 4 - Effect of New Hydro Record on Monthly LOLP

# Other Adequacy Metrics

Table 2 - Adequacy Metric Definitions

| Metric | Description |
| --- | --- |
| LOLP | Loss of load probability = number of games with a problem divided by the total number of games (in percent) |
| USRP | Use of standby resource probability = Number of games that dispatch standby resources at least once divided by total games (in percent) |
| CVaR (energy) | Conditional value at risk, energy = average annual curtailment for 5% worst games (in megawatt-hours) |
| CVaR (peak) | Conditional value at risk, peak = average single-hour curtailment for worst 5% of games (in megawatts) |
| EUE | Expected unserved energy = total curtailment divided by the total number of games (in megawatt-hours) |
| LOLH | Loss of load hours = total number of hours of curtailment divided by total number of games (in hours) |
| PGC | Percent of games with curtailment = Use of Standby Resources (in percent) |

Table 3 - Adequacy Measures for 2017

| Adequacy Metrics |  |  |
| --- | --- | --- |
| Metric | Value | Units |
| LOLP | 6.6 | Percent |
| Use SR | 9.7 | Percent |
| CVaR (energy) | 99000 | MW-hours |
| CVaR (peak) | 4000 | MW |
| EUE | 5000 | MW-hours |
| LOLH | 2.7 | Hours/year |
| % Games w/Curt | 9.7 | Percent |

# Dealing with Uncertainties

Figure 5 - Load and SW Market Impacts to LOLP

Figure 6 - Load and SW Market Uncertainty LOLP Map

Figure 7 - Illustrative Example of LOLP Likelihood based on Load & Market Uncertainty

# Reliance on Market Supply

The current adequacy methodology assumes that all reasonably available resources will be dispatched to avoid shortfalls.  In this sense, the analysis represents the likelihood that demand will be served, cost notwithstanding.  It is not intended to be a resource needs assessment, when costs and other factors are considered.  But for this analysis, non-firm resources are included.   These resources include regional Independent Power Producer (IPP) generation, out-of-region markets (primarily from the Southwest) and the use of borrowed hydro, which is energy derived by using water below the drafting rights elevation.

The general dispatch order for these resources is to first buy from IPPs, secondly to buy from out-of-region markets and lastly to use borrowed hydro energy.  When borrowed hydro is used, it is replaced as quickly as possible, even if it means buying from out-of-region markets at a later time.

Figure 3 below illustrates the expected likelihood of use for each of these three types of non-firm resources by month.  It should be noted that the SW market on-peak purchases are limited to the winter months only.  Also modeled, but still under debate, is the availability of light load hour purchases made in advance of potential peak hour problems.  This purchase-ahead resource is limited to 1,000 megawatts in any light load hour and is called upon only when borrowed hydro is expected to be used during the next peak demand period.

Figure 4 shows the average contribution from each resource by month.  However, average values are not always very informative.  Thus, Figures 5-8 provide the dispatch probability curves for these 4 non-firm resources.

Figure 8 - Monthly Energy Market Purchase Probability

Figure 9 - Hourly Market Purchase Probability (All Hours)

Figure 10 - Hourly Market Purchase Probability by Month

# Generating Resources Dispatch

Table 4 - Average Resource Dispatch by Month

|  | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | Ann |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nuclear | 973 | 1015 | 1022 | 1024 | 1026 | 1027 | 1024 | 0 | 0 | 1023 | 1025 | 1024 | 849 |
| Coal | 3998 | 3834 | 3767 | 3326 | 3150 | 2845 | 1449 | 447 | 931 | 2329 | 3728 | 4217 | 2835 |
| Gas | 2964 | 1571 | 1589 | 1674 | 1490 | 1062 | 535 | 401 | 634 | 921 | 1855 | 2534 | 1436 |
| Wind | 1044 | 1078 | 1061 | 1130 | 1157 | 1369 | 1629 | 1553 | 1480 | 1363 | 1218 | 1036 | 1260 |
| Market | 666 | 1194 | 1168 | 1200 | 1028 | 710 | 193 | 21 | 84 | 147 | 402 | 550 | 614 |

Figure 11 - Wind Generation Probability by Month

Figure 12 - Gas-Fired Generation Dispatch Probability by Month

Figure 13 - Coal-Fired Generation Dispatch Probability by Month

Figure 14 - Nuclear Generation Dispatch Probability by Month

# Curtailment Statistics

Sometimes, simply looking at simulation results can provide insight into the behavior of the power system.  Table 5 below summarizes a few statistics for the curtailment events reported in our analysis.  It should be noted that this particular study was only run with 210 simulations and thus the statistics for curtailment events (as well as the adequacy measures) will have a larger error range.

Besides looking at curtailment statistics, it may also be of great use to examine what conditions existed during the time of each shortfall.  Thus, a record of all curtailment events along with the values for the four random variables used in the analysis will be provided in a separate spreadsheet (available on the Forum’s website).  The four random variables displayed in the spreadsheet are;

- Water supply, as a percentage of monthly runoff volume

- Temperature, as a percentage of that day’s historical temperature range

- Wind generation, based on historical wind capacity factors from BPA’s wind fleet

- Forced outage conditions

Some attempts have been made to correlate shortfall events with the occurrence of certain temperatures, water conditions, wind generation patterns and forced outages, but unfortunately without much success.  This is an area of study that should be explored further.

Table 5 – Curtailment Statistics

| Statistic | Value | Units |
| --- | --- | --- |
| Exp Events/year | 0.21 | Events |
| Avg Event Duration | 13 | Hours |
| Avg Event Magnitude | 24,361 | MW-hrs |
| Avg Event Peak | 1,764 | MW |
| Exp Curt Hrs/year | 2.7 | Hours |
| LOLP | 6.6 | % |

Figure 15 - Curtailment Event Duration Probability

Figure 16 - Curtailment Magnitude Probability

Figure 17 - Curtailment Magnitude Probability for Events Less than 4 Hours

Figure 18 - Curtailment Event Magnitude vs. Duration

Table 6 - Sample Curtailment Event Record

| Event | Game | Month | DUR | MAG | Peak | Hydro % | Temp % | Wind % | FO % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | Feb | 1 | 254 | 254 | 39 | 87 | 0 | 16 |
| 2 | 2 | Feb | 2 | 1304 | 652 | 39 | 87 | 0 | 16 |
| 3 | 3 | Jan | 24 | 22216 | 2884 | 3 | 72 | 3 | 4 |
| 4 | 3 | Jan | 74 | 145122 | 5401 | 3 | 73 | 25 | 3 |
| 5 | 3 | Jan | 39 | 55649 | 3707 | 3 | 76 | 5 | 2 |
| 6 | 3 | Jan | 2 | 2285 | 1716 | 3 | 77 | 31 | 1 |
| 7 | 3 | Jan | 2 | 2450 | 1527 | 3 | 83 | 0 | 4 |
| 8 | 3 | Jan | 1 | 403 | 403 | 3 | 83 | 2 | 4 |
| 9 | 8 | Jan | 10 | 27369 | 4637 | 14 | 85 | 1 | 7 |
| 10 | 9 | Feb | 1 | 769 | 769 | 0 | 47 | 17 | 12 |
| 11 | 9 | Feb | 3 | 2218 | 1317 | 0 | 48 | 29 | 10 |
| 12 | 9 | Feb | 2 | 1504 | 789 | 0 | 49 | 11 | 10 |
| 13 | 9 | Feb | 7 | 5874 | 1192 | 0 | 59 | 2 | 5 |
| 14 | 16 | Jan | 6 | 538 | 95 | 5 | 100 | 9 | 2 |
| 15 | 16 | Jan | 2 | 3144 | 3095 | 5 | 80 | 33 | 7 |
| 16 | 47 | Jan | 2 | 1188 | 1135 | 49 | 43 | 8 | 15 |
| 17 | 49 | Aug | 17 | 4636 | 599 | 23 | 94 | 0 | 15 |
| 18 | 77 | Sep | 2 | 351 | 181 | 9 | 57 | 14 | 15 |
| 19 | 80 | Oct | 1 | 5 | 5 | 46 | 22 | 16 | 21 |
| 20 | 80 | Jan | 2 | 689 | 455 | 25 | 89 | 3 | 4 |
| 21 | 83 | Feb | 40 | 85662 | 4443 | 4 | 72 | 1 | 4 |
| 22 | 100 | Feb | 1 | 111 | 111 | 46 | 43 | 0 | 4 |
| 23 | 100 | Feb | 2 | 2464 | 1470 | 46 | 43 | 1 | 4 |
| 24 | 100 | Feb | 2 | 3251 | 2022 | 46 | 43 | 4 | 8 |
| 25 | 100 | Feb | 2 | 735 | 439 | 46 | 69 | 1 | 8 |
| 26 | 109 | Jan | 1 | 35 | 35 | 28 | 31 | 16 | 6 |
| 27 | 129 | Jan | 2 | 1394 | 1014 | 9 | 66 | 4 | 2 |
| 28 | 129 | Jun | 5 | 3616 | 1021 | 1 | 17 | 3 | 15 |
| 29 | 144 | Aug | 7 | 782 | 125 | 3 | 65 | 16 | 12 |
| 30 | 146 | Feb | 1 | 40 | 40 | 5 | 76 | 3 | 2 |
| 31 | 146 | Feb | 2 | 882 | 821 | 5 | 76 | 22 | 3 |
| 32 | 153 | Jun | 4 | 976 | 452 | 0 | 34 | 2 | 8 |
| 33 | 154 | Jan | 47 | 89309 | 4222 | 62 | 52 | 2 | 4 |
| 34 | 160 | Oct | 12 | 8041 | 856 | 46 | 44 | 15 | 29 |
| 35 | 163 | Feb | 2 | 736 | 554 | 4 | 53 | 8 | 15 |
| 36 | 163 | Feb | 22 | 14166 | 2412 | 4 | 53 | 5 | 15 |
| 37 | 163 | Feb | 2 | 2375 | 1625 | 4 | 64 | 8 | 8 |
| 38 | 163 | Feb | 3 | 3831 | 2000 | 4 | 64 | 1 | 10 |
| 39 | 163 | Aug | 6 | 2299 | 468 | 13 | 39 | 2 | 11 |
| 40 | 163 | Aug | 12 | 4781 | 574 | 13 | 53 | 3 | 14 |
| 41 | 164 | Jan | 116 | 346473 | 6087 | 10 | 65 | 15 | 4 |
| 42 | 164 | Jan | 20 | 29032 | 3135 | 10 | 75 | 59 | 4 |
| 43 | 164 | Jan | 2 | 2331 | 1427 | 10 | 82 | 0 | 2 |
| 44 | 164 | Feb | 1 | 258 | 258 | 11 | 59 | 2 | 2 |
| Event | Game | Month | DUR | MAG | Peak | Hydro % | Temp % | Wind % | FO % |
| 45 | 169 | Jan | 26 | 44782 | 4468 | 0 | 66 | 1 | 3 |
| 46 | 169 | Jan | 2 | 3456 | 1728 | 0 | 67 | 16 | 2 |
| 47 | 177 | Jan | 24 | 24942 | 2896 | 30 | 62 | 8 | 9 |
| 48 | 177 | Jan | 71 | 232974 | 7500 | 30 | 61 | 28 | 11 |
| 49 | 177 | Feb | 72 | 248783 | 6750 | 32 | 61 | 3 | 4 |
| 50 | 220 | Nov | 1 | 702 | 702 | 4 | 59 | 12 | 10 |
| 51 | 220 | Jan | 1 | 300 | 300 | 11 | 86 | 5 | 10 |
| 52 | 220 | Jan | 2 | 1917 | 1086 | 11 | 86 | 3 | 10 |
| 53 | 233 | Feb | 2 | 443 | 325 | 10 | 87 | 0 | 10 |
| 54 | 235 | Dec | 1 | 48 | 48 | 19 | 92 | 14 | 7 |
| 55 | 252 | Oct | 12 | 2348 | 245 | 33 | 29 | 1 | 23 |
| 56 | 252 | Oct | 1 | 73 | 73 | 33 | 29 | 1 | 22 |
| 57 | 253 | Jan | 4 | 323 | 97 | 33 | 0 | 21 | 4 |
| 58 | 253 | Jan | 3 | 3305 | 1748 | 33 | 2 | 4 | 1 |
| 59 | 253 | Jan | 2 | 2069 | 1287 | 33 | 7 | 0 | 1 |
| 60 | 254 | Feb | 54 | 86704 | 4192 | 47 | 57 | 3 | 3 |
| 61 | 254 | Feb | 2 | 2251 | 1126 | 47 | 73 | 6 | 2 |
| 62 | 256 | Jan | 2 | 1661 | 1270 | 5 | 63 | 20 | 11 |
| 63 | 279 | Sep | 7 | 1837 | 276 | 62 | 15 | 0 | 22 |
| 64 | 289 | Dec | 1 | 253 | 253 | 11 | 28 | 6 | 11 |
| 65 | 289 | Dec | 2 | 2013 | 1006 | 11 | 28 | 33 | 12 |
| 66 | 300 | Feb | 1 | 1333 | 1333 | 15 | 76 | 3 | 4 |
| 67 | 300 | Feb | 4 | 4248 | 2355 | 15 | 76 | 20 | 4 |
| 68 | 300 | Feb | 27 | 21275 | 2502 | 15 | 72 | 10 | 2 |
| 69 | 300 | Feb | 2 | 2254 | 1644 | 15 | 72 | 12 | 1 |
| 70 | 300 | Feb | 2 | 1900 | 1504 | 15 | 72 | 1 | 1 |
| 71 | 313 | Dec | 41 | 78744 | 3842 | 14 | 87 | 8 | 11 |
| 72 | 313 | Dec | 2 | 965 | 655 | 14 | 85 | 4 | 8 |
| 73 | 313 | Dec | 2 | 703 | 610 | 14 | 90 | 0 | 5 |
| 74 | 313 | Dec | 2 | 3770 | 2038 | 14 | 90 | 0 | 3 |
| 75 | 313 | Dec | 2 | 1584 | 1328 | 14 | 82 | 0 | 3 |
| 76 | 313 | Dec | 13 | 8477 | 2490 | 14 | 82 | 0 | 9 |
| 77 | 313 | Dec | 1 | 601 | 601 | 14 | 63 | 1 | 9 |
| 78 | 314 | Feb | 2 | 158 | 79 | 30 | 73 | 0 | 3 |
| 79 | 323 | Jan | 55 | 117446 | 5000 | 3 | 64 | 7 | 4 |
| 80 | 330 | Aug | 13 | 203 | 29 | 22 | 62 | 16 | 9 |
| 81 | 331 | Feb | 54 | 125787 | 5417 | 6 | 57 | 3 | 3 |
| 82 | 333 | Jan | 3 | 1073 | 533 | 33 | 67 | 37 | 8 |
| 83 | 353 | Dec | 6 | 49 | 8 | 27 | 76 | 3 | 7 |
| 84 | 353 | Dec | 2 | 26 | 13 | 27 | 76 | 30 | 7 |
| 85 | 380 | Sep | 7 | 2247 | 426 | 4 | 34 | 0 | 19 |
| 86 | 385 | Jan | 68 | 254051 | 8755 | 15 | 54 | 6 | 10 |

Table 7 - Sample Energy Curtailment Distribution by Month

| Game | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Ann Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | 1048 |  |  |  |  |  |  |  |  | 1048 |
| 3 |  |  |  | 336263 |  |  |  |  |  |  |  |  | 336263 |
| 8 |  |  |  | 24726 |  |  |  |  |  |  |  |  | 24726 |
| 16 |  |  |  | 25714 |  |  |  |  |  |  |  |  | 25714 |
| 17 |  |  | 105 |  |  |  |  |  |  |  |  |  | 105 |
| 57 |  |  |  |  |  |  |  |  |  |  | 6209 |  | 6209 |
| 73 |  |  |  |  |  |  |  |  | 444 |  |  |  | 444 |
| 82 |  |  | 16649 |  |  |  |  |  |  |  |  |  | 16649 |
| 100 |  |  |  |  | 4084 |  |  |  |  |  |  |  | 4084 |
| 129 |  |  |  | 1721 |  |  |  |  |  |  |  |  | 1721 |
| 143 | 1295 |  |  |  |  |  |  |  |  |  |  |  | 1295 |
| 146 |  |  |  |  | 322 |  |  |  |  |  |  |  | 322 |
| 154 |  |  |  | 72415 |  |  |  |  |  |  |  |  | 72415 |
| 159 | 16661 |  |  |  |  |  |  |  |  |  |  |  | 16661 |
| 160 |  |  |  |  | 4150 |  |  |  |  |  |  |  | 4150 |
| 163 |  |  |  |  | 387 |  |  |  |  |  |  |  | 387 |
| 164 |  |  |  | 391937 | 5494 |  |  |  |  |  |  |  | 397432 |
| 169 |  |  |  | 241795 |  |  |  |  |  |  |  |  | 241795 |
| 173 |  |  |  |  |  |  |  |  |  |  |  | 9520 | 9520 |
| 176 |  |  |  | 11921 |  |  |  |  |  |  |  |  | 11921 |
| 177 |  |  |  | 164589 | 317574 |  |  |  |  |  |  |  | 482163 |
| 233 |  |  |  |  |  |  |  |  | 4281 |  |  |  | 4281 |
| 234 | 1193 |  |  |  |  |  |  |  |  |  |  |  | 1193 |
| 253 |  |  |  | 79399 |  |  |  |  |  |  | 4796 |  | 84194 |
| 254 |  |  |  |  | 93209 |  |  |  |  |  |  |  | 93209 |
| 289 |  |  | 295 |  |  |  |  |  |  |  |  |  | 295 |
| 300 |  |  |  |  | 47986 |  |  |  |  |  |  |  | 47986 |
| 314 |  |  |  |  | 4647 |  |  |  |  |  |  |  | 4647 |
| 316 |  |  |  | 10127 |  |  |  |  |  |  |  |  | 10127 |
| 323 |  |  |  | 214220 |  |  |  |  |  |  |  |  | 214220 |
| 331 |  |  |  |  | 161312 |  |  |  |  |  |  |  | 161312 |
| 333 | 369 |  |  |  |  |  |  |  |  |  |  |  | 369 |
| 385 |  |  |  | 254709 |  |  |  |  |  |  |  |  | 254709 |
| 393 |  |  |  | 5081 |  |  |  |  |  |  |  |  | 5081 |
| 395 |  |  |  | 841 |  |  |  |  |  |  |  |  | 841 |
| 408 |  |  |  | 162356 | 319586 |  |  |  |  |  |  | 167 | 482109 |
| 413 |  | 145 |  |  |  |  |  |  |  |  |  |  | 145 |
| 417 |  |  |  | 182428 |  |  |  |  |  |  |  |  | 182428 |
| 451 |  |  |  |  |  |  |  |  |  |  | 4895 |  | 4895 |
| 465 |  |  |  | 225029 |  |  |  |  |  |  |  |  | 225029 |
| 484 |  |  |  | 295395 | 95 |  |  |  |  |  |  |  | 295490 |
| 485 |  |  |  |  | 1017 |  |  |  |  |  |  |  | 1017 |
| 494 |  |  |  | 26312 |  |  |  |  |  |  |  |  | 26312 |
| 501 |  |  |  |  |  |  |  |  |  |  | 10120 |  | 10120 |
| Game | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Ann Total |
| 529 |  |  |  |  |  |  |  |  |  |  | 5167 |  | 5167 |
| 539 |  |  |  | 48875 |  |  |  |  |  |  |  |  | 48875 |
| 545 |  |  |  |  | 48613 |  |  |  |  |  |  |  | 48613 |
| 554 | 3652 |  |  |  |  |  |  |  |  |  |  |  | 3652 |
| 555 |  |  |  |  |  |  |  |  |  |  |  | 5839 | 5839 |
| 562 |  |  |  | 171748 | 244300 |  |  |  |  |  |  |  | 416049 |
| 564 |  |  |  | 65629 |  |  |  |  |  |  |  |  | 65629 |
| 571 |  |  |  | 26697 |  |  |  |  |  |  |  |  | 26697 |
| 577 |  |  | 569 |  |  |  |  |  |  |  |  |  | 569 |
| 602 |  |  | 852 |  |  |  |  |  |  |  |  |  | 852 |
| 620 |  |  | 1037 |  |  |  |  |  |  |  |  |  | 1037 |
| 624 |  |  |  | 50266 |  |  |  |  |  |  |  |  | 50266 |
| 625 |  |  |  |  | 4086 |  |  |  |  |  |  |  | 4086 |
| 634 | 1157 |  |  |  |  |  |  |  |  |  |  |  | 1157 |
| 639 |  |  |  |  | 115599 |  |  |  |  |  |  |  | 115599 |
| 644 |  | 217 |  |  |  |  |  |  |  |  |  |  | 217 |
| 648 |  |  |  | 91825 |  |  |  |  |  |  |  |  | 91825 |
| 701 |  |  |  | 93484 |  |  |  |  |  |  |  |  | 93484 |
| 715 |  |  |  |  |  |  |  |  |  |  | 17377 |  | 17377 |
| 716 |  |  |  |  | 302432 |  |  |  |  |  |  |  | 302432 |
| 729 |  |  |  | 84910 |  |  |  |  |  |  |  |  | 84910 |
| 780 |  |  |  | 60342 |  |  |  |  |  |  |  |  | 60342 |
| 785 |  |  |  | 270054 |  |  |  |  |  |  |  |  | 270054 |
| 793 |  |  |  | 3811 | 313564 |  |  |  |  |  |  | 7999 | 325375 |
| 795 |  |  |  | 1109 |  |  |  |  |  |  |  |  | 1109 |
| 797 | 7464 |  |  |  |  |  |  |  |  |  |  |  | 7464 |
| 802 |  |  |  | 148685 |  |  |  |  |  |  |  |  | 148685 |
| 816 |  |  |  | 18768 |  |  |  |  |  |  | 182 |  | 18950 |
| 817 |  |  |  | 83512 |  |  |  |  |  |  |  |  | 83512 |
| 852 |  |  | 21466 |  |  |  |  |  |  |  |  |  | 21466 |
| 857 |  |  |  | 474 |  |  |  |  |  |  |  |  | 474 |
| 870 |  |  |  |  | 28915 |  |  |  |  |  |  |  | 28915 |
| 875 | 6225 |  |  |  |  |  |  |  |  |  | 12241 |  | 18466 |
| 883 |  |  |  | 9157 |  |  |  |  |  |  |  |  | 9157 |
| 889 |  |  |  |  | 83 |  |  |  |  |  |  |  | 83 |
| 891 |  |  |  |  |  |  |  |  |  |  | 450 |  | 450 |
| 893 |  |  |  | 7437 |  |  |  |  |  |  |  |  | 7437 |
| 905 |  | 3366 |  |  |  |  |  |  |  |  |  |  | 3366 |
| 929 |  |  | 29300 |  |  |  |  |  |  |  |  |  | 29300 |
| 946 |  |  |  | 15108 |  |  |  |  |  |  |  |  | 15108 |
| 947 |  |  |  |  | 16369 |  |  |  |  |  |  |  | 16369 |

Table 8 - Sample Peak Hour Curtailment Distribution by Month

| Game | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Max |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | 579 |  |  |  |  |  |  |  |  | 579 |
| 3 |  |  |  | 7053 |  |  |  |  |  |  |  |  | 7053 |
| 8 |  |  |  | 4093 |  |  |  |  |  |  |  |  | 4093 |
| 16 |  |  |  | 3505 |  |  |  |  |  |  |  |  | 3505 |
| 17 |  |  | 105 |  |  |  |  |  |  |  |  |  | 105 |
| 57 |  |  |  |  |  |  |  |  |  |  | 773 |  | 773 |
| 73 |  |  |  |  |  |  |  |  | 328 |  |  |  | 328 |
| 82 |  |  | 2763 |  |  |  |  |  |  |  |  |  | 2763 |
| 100 |  |  |  |  | 1593 |  |  |  |  |  |  |  | 1593 |
| 129 |  |  |  | 999 |  |  |  |  |  |  |  |  | 999 |
| 143 | 547 |  |  |  |  |  |  |  |  |  |  |  | 547 |
| 146 |  |  |  |  | 322 |  |  |  |  |  |  |  | 322 |
| 154 |  |  |  | 4355 |  |  |  |  |  |  |  |  | 4355 |
| 159 | 637 |  |  |  |  |  |  |  |  |  |  |  | 637 |
| 160 |  |  |  |  | 1700 |  |  |  |  |  |  |  | 1700 |
| 163 |  |  |  |  | 387 |  |  |  |  |  |  |  | 387 |
| 164 |  |  |  | 6362 | 2078 |  |  |  |  |  |  |  | 6362 |
| 169 |  |  |  | 5417 |  |  |  |  |  |  |  |  | 5417 |
| 173 |  |  |  |  |  |  |  |  |  |  |  | 903 | 903 |
| 176 |  |  |  | 2087 |  |  |  |  |  |  |  |  | 2087 |
| 177 |  |  |  | 5848 | 8542 |  |  |  |  |  |  |  | 8542 |
| 233 |  |  |  |  |  |  |  |  | 420 |  |  |  | 420 |
| 234 | 185 |  |  |  |  |  |  |  |  |  |  |  | 185 |
| 253 |  |  |  | 3511 |  |  |  |  |  |  | 334 |  | 3511 |
| 254 |  |  |  |  | 4382 |  |  |  |  |  |  |  | 4382 |
| 289 |  |  | 295 |  |  |  |  |  |  |  |  |  | 295 |
| 300 |  |  |  |  | 2815 |  |  |  |  |  |  |  | 2815 |
| 314 |  |  |  |  | 1242 |  |  |  |  |  |  |  | 1242 |
| 316 |  |  |  | 2861 |  |  |  |  |  |  |  |  | 2861 |
| 323 |  |  |  | 5527 |  |  |  |  |  |  |  |  | 5527 |
| 331 |  |  |  |  | 5357 |  |  |  |  |  |  |  | 5357 |
| 333 | 106 |  |  |  |  |  |  |  |  |  |  |  | 106 |
| 385 |  |  |  | 8956 |  |  |  |  |  |  |  |  | 8956 |
| 393 |  |  |  | 3492 |  |  |  |  |  |  |  |  | 3492 |
| 395 |  |  |  | 417 |  |  |  |  |  |  |  |  | 417 |
| 408 |  |  |  | 5072 | 8236 |  |  |  |  |  |  | 29 | 8236 |
| 413 |  | 145 |  |  |  |  |  |  |  |  |  |  | 145 |
| 417 |  |  |  | 6522 |  |  |  |  |  |  |  |  | 6522 |
| 451 |  |  |  |  |  |  |  |  |  |  | 319 |  | 319 |
| 465 |  |  |  | 6697 |  |  |  |  |  |  |  |  | 6697 |
| 484 |  |  |  | 5062 | 95 |  |  |  |  |  |  |  | 5062 |
| 485 |  |  |  |  | 751 |  |  |  |  |  |  |  | 751 |
| 494 |  |  |  | 2530 |  |  |  |  |  |  |  |  | 2530 |
| Game | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Max |
| 501 |  |  |  |  |  |  |  |  |  |  | 704 |  | 704 |
| 529 |  |  |  |  |  |  |  |  |  |  | 880 |  | 880 |
| 539 |  |  |  | 3657 |  |  |  |  |  |  |  |  | 3657 |
| 545 |  |  |  |  | 4642 |  |  |  |  |  |  |  | 4642 |
| 554 | 335 |  |  |  |  |  |  |  |  |  |  |  | 335 |
| 555 |  |  |  |  |  |  |  |  |  |  |  | 1026 | 1026 |
| 562 |  |  |  | 5491 | 5793 |  |  |  |  |  |  |  | 5793 |
| 564 |  |  |  | 3208 |  |  |  |  |  |  |  |  | 3208 |
| 571 |  |  |  | 2702 |  |  |  |  |  |  |  |  | 2702 |
| 577 |  |  | 118 |  |  |  |  |  |  |  |  |  | 118 |
| 602 |  |  | 505 |  |  |  |  |  |  |  |  |  | 505 |
| 620 |  |  | 1037 |  |  |  |  |  |  |  |  |  | 1037 |
| 624 |  |  |  | 4429 |  |  |  |  |  |  |  |  | 4429 |
| 625 |  |  |  |  | 1218 |  |  |  |  |  |  |  | 1218 |
| 634 | 202 |  |  |  |  |  |  |  |  |  |  |  | 202 |
| 639 |  |  |  |  | 4862 |  |  |  |  |  |  |  | 4862 |
| 644 |  | 217 |  |  |  |  |  |  |  |  |  |  | 217 |
| 648 |  |  |  | 5118 |  |  |  |  |  |  |  |  | 5118 |
| 701 |  |  |  | 5862 |  |  |  |  |  |  |  |  | 5862 |
| 715 |  |  |  |  |  |  |  |  |  |  | 1292 |  | 1292 |
| 716 |  |  |  |  | 7727 |  |  |  |  |  |  |  | 7727 |
| 729 |  |  |  | 6161 |  |  |  |  |  |  |  |  | 6161 |
| 780 |  |  |  | 4528 |  |  |  |  |  |  |  |  | 4528 |
| 785 |  |  |  | 5587 |  |  |  |  |  |  |  |  | 5587 |
| 793 |  |  |  | 1508 | 7743 |  |  |  |  |  |  | 527 | 7743 |
| 795 |  |  |  | 92 |  |  |  |  |  |  |  |  | 92 |
| 797 | 756 |  |  |  |  |  |  |  |  |  |  |  | 756 |
| 802 |  |  |  | 5753 |  |  |  |  |  |  |  |  | 5753 |
| 816 |  |  |  | 2774 |  |  |  |  |  |  | 61 |  | 2774 |
| 817 |  |  |  | 3632 |  |  |  |  |  |  |  |  | 3632 |
| 852 |  |  | 3400 |  |  |  |  |  |  |  |  |  | 3400 |
| 857 |  |  |  | 237 |  |  |  |  |  |  |  |  | 237 |
| 870 |  |  |  |  | 2857 |  |  |  |  |  |  |  | 2857 |
| 875 | 1381 |  |  |  |  |  |  |  |  |  | 943 |  | 1381 |
| 883 |  |  |  | 4094 |  |  |  |  |  |  |  |  | 4094 |
| 889 |  |  |  |  | 83 |  |  |  |  |  |  |  | 83 |
| 891 |  |  |  |  |  |  |  |  |  |  | 88 |  | 88 |
| 893 |  |  |  | 1711 |  |  |  |  |  |  |  |  | 1711 |
| 905 |  | 666 |  |  |  |  |  |  |  |  |  |  | 666 |
| 929 |  |  | 3044 |  |  |  |  |  |  |  |  |  | 3044 |
| 946 |  |  |  | 2213 |  |  |  |  |  |  |  |  | 2213 |
| 947 |  |  |  |  | 2179 |  |  |  |  |  |  |  | 2179 |

# Appendix A – Assumptions

2017 Pacific Northwest Resource Adequacy Assessment

Study Parameters

Main Parameters

Operating Year:				October 2016 through September 2017

Simulation Mode:			Each hour of the year

Random Variable Settings

Number of games:			6,160

Water year selection:			Sequential (because Canadian operation is fixed)

Water years selected:			80 years, 1929 through 2008

Temperature year selection:		Random

Temperature years selected:		77 years, 1929 through 2005 (to match wind year data)

Wind year selection:			Lockstep with temperature

Wind years selected:			77-year temperature correlated synthetic set

Stochastic forced outage:		Yes

Market and Wind Assumptions

Nameplate wind capacity:		4,579 MW

NW Market winter:			Full IPP = 3,451 MW

NW Market summer:			1,000 MW

SW Market on-peak winter:		1,700 MW

SW Market off-peak winter:		3,000 MW (purchase ahead)

SW Market on-peak summer:		0 MW

SW Market off-peak summer:		3,000 MW (purchase ahead)

Maximum import limit:			3,200 MW

Resource Assumptions

Columbia Generating Station:		On maintenance May and June

Hydro INC/DEC requirements:		900/1,100 MW (4K wind Peak vs. Energy file)

Thermal seasonal capacity:		Off (not sufficient data)

Thermal ramp rates:			Not yet implemented

Coal day-must-run:			On (if coal dispatched, must run at least one day)

Forced outages:				Stochastic for each plant (if on FOR, plant is out)

Maintenance:	Each plant derated for aggregate thermal maintenance rate (Same method and data used in AURORAxmp)

Borrowed Hydro:			1,000 MW-months maximum

(Hydro energy below drafting-rights elevation)

Operating reserves thermal:		7 percent

Operating reserves hydro:		5 percent

Load Assumptions

Hourly loads:				Council’s Short-Term Model (econometric)

77 load years based on temps from 1929-2005

Conservation:				6th Power Plan target level, included in the hourly loads

Pumping loads:				Included in the hourly loads

Transmission losses:			Included in the hourly loads

Standby Resource Assumptions

# Appendix B – 2017 Resources and Loads

Table 9 - Northwest Resources including NW Market Resources

| Name | Type | NW | FOR | IPP |
| --- | --- | --- | --- | --- |
| 1910 Meyers Falls | Hyd | 0 | 0 |  |
| Alden Bailey (Wauna Peaking/Loki) | GT | 11 | 0.051 |  |
| Amalgamated Sugar (TASCO) (Nampa) 1 - 3 | Coal | 0 | 0.07 |  |
| Amalgamated Sugar (TASCO) (Twin Falls) 1-3 | Coal | 0 | 0.07 |  |
| Amy Ranch | Hyd | 1 | 0 |  |
| Barber Dam | Hyd | 3 | 0 |  |
| Basin Creek 1 - 9 | IC | 17 | 0.047 |  |
| Beaver 1 - 7 | CCCT | 509 | 0.059 |  |
| Beaver 8 | GT | 20 | 0.051 |  |
| Bennett Mountain | GT | 180 | 0.051 |  |
| Bettencourt B6 Dairy (Cargill) | IC | 2 | 0.047 |  |
| Bettencourt Dry Creek Biofactory (Cargill) | IC | 2 | 0.047 |  |
| Big Hanaford CC 1A-1E | CCCT | 0 | 0.059 | 248 |
| Big Sheep Creek | Hyd | 2 | 0 |  |
| Big Sky West Dairy Digester | IC | 1 | 0.047 |  |
| Biomass One 1 & 2 | STCG | 25 | 0.07 |  |
| Birch Creek | Hyd | 1 | 0 |  |
| Black Creek | Hyd | 4 | 0 |  |
| Black Eagle 1 - 3 | Hyd | 0 | 0 |  |
| Blind Canyon | Hyd | 0 | 0 |  |
| Boardman | Coal | 435 | 0.067 |  |
| Boise 1 & 2 (Medford) | Biomass ST | 9 | 0.07 |  |
| Boulder Park 1-6 | IC | 25 | 0.047 |  |
| Boundary GT | IC | 1 | 0.047 |  |
| Box Canyon | Hyd | 0 | 0 |  |
| Box Canyon 1 & 2 | Hyd | 3 | 0 |  |
| Briggs Creek | Hyd | 1 | 0 |  |
| Broadwater Toston Dam | Hyd | 1 | 0 |  |
| Bull Run No. 1 (Portland Hydro) | Hyd | 18 | 0 |  |
| Bull Run No. 2 (Portland Hydro) | Hyd | 0 | 0 |  |
| Bypass | Hyd | 4 | 0 |  |
| Cedar Draw Creek (Crystal Springs) | Hyd | 1 | 0 |  |
| Central Oregon Siphon | Hyd | 0 | 0 |  |
| Centralia 1IPP | Coal | 0 | 0.067 | 290 |
| Centralia 1PSE | Coal | 380 | 0.067 |  |
| Centralia 2 | Coal | 0 | 0.067 | 670 |
| Chehalis Generating Facility | CCCT | 514 | 0.059 |  |
| Chester Diversion | Hyd | 3 | 0 |  |
| City of Albany (Vine Street WTP) | Hyd | 1 | 0 |  |
| Clearwater Hatchery (Dworshak) | Hyd | 3 | 0 |  |
| Name | Type | NW | FOR | IPP |
| Clearwater Paper 1 - 4 | STCG | 75 | 0.07 |  |
| Cochrane 1 & 2 | Hyd | 0 | 0 |  |
| Coffin Butte 1 - 5 | IC | 6 | 0.047 |  |
| Cogen II (D.R. Johnson) 1 & 2 | STCG | 8 | 0.07 |  |
| Colstrip 1 | Coal | 154 | 0.067 |  |
| Colstrip 2 | Coal | 154 | 0.067 |  |
| Colstrip 3 | Coal | 518 | 0.067 |  |
| Colstrip 4 | Coal | 681 | 0.067 |  |
| Columbia Blvd Wastewater Treatment Plant | IC | 2 | 0.047 |  |
| Columbia Generating Station | Nuclear | 1130 | 0.0885 |  |
| Columbia Ridge Landfill | IC | 12 | 0.047 |  |
| Colville Indian Power & Veneer 1 & 2 | STCG | 1 | 0.07 |  |
| COPCO 1 (1 & 2) | Hyd | 24 | 0 |  |
| COPCO 2 (1 & 2) | Hyd | 32 | 0 |  |
| Corrette (J.E. Corette) | Coal | 0 | 0.067 |  |
| Covanta Marion | MSW | 13 | 0.07 |  |
| Cowiche Hydroelectric Project | Hyd | 0 | 0 |  |
| Coyote Springs 1 | CCCT | 259 | 0.059 |  |
| Coyote Springs 2 | CCCT | 301 | 0.059 |  |
| Crystal Mountain | IC | 3 | 0.047 |  |
| Danskin (Evander Andrews) CT1 | GT | 183 | 0.051 |  |
| Danskin (Evander Andrews) CT2 (ex. Danskin 1) | GT | 47 | 0.051 |  |
| Danskin (Evander Andrews) CT3 (ex. Danskin 2) | GT | 47 | 0.051 |  |
| Deep Creek | Hyd | 0 | 0 |  |
| DeRuyter Dairy | IC | 1 | 0.047 |  |
| Dietrich Drop | Hyd | 2 | 0 |  |
| Don Plant (Simplot Pocatello) | STCG | 8 | 0.07 |  |
| Double A Dairy | IC | 1 | 0.047 |  |
| Douglas County Forest Products | STCG | 3 | 0.07 |  |
| Dry Creek | Hyd | 0 | 0 |  |
| Dry Creek Landfill | IC | 2 | 0.047 |  |
| Elk Creek (El Dorado Hydro Elk Creek) | Hyd | 0 | 0 |  |
| Eltopia Branch Canal 4.6 | Hyd | 0 | 0 |  |
| Encogen 1-4 | CCCT | 179 | 0.059 |  |
| Evergreen Forest Products (Tamarack) | STCG | 4 | 0.07 |  |
| Fall Creek 1 - 3 | Hyd | 2 | 0 |  |
| Falls River | Hyd | 4 | 0 |  |
| Falls Creek | Hyd | 1 | 0 |  |
| Farm Power Lynden | IC | 1 | 0.047 |  |
| Farm Power Rexville | IC | 1 | 0.047 |  |
| Farmers Irr. Dist. No. 2 (Copper Dam) | Hyd | 5 | 0 |  |
| Farmers Irr. Dist. No. 3 (Peters Drive) | Hyd | 0 | 0 |  |
| Faulkner | Hyd | 0 | 0 |  |
| Finley Buttes Regional Landfill | IC | 3 | 0.047 |  |
| Flathead County Landfill | IC | 2 | 0.047 |  |
| Name | Type | NW | FOR | IPP |
| Ford | Hyd | 0 | 0 |  |
| Fortix | IC | 1 | 0.047 |  |
| Frederickson 1 | GT | 80 | 0.051 |  |
| Frederickson 2 | GT | 80 | 0.051 |  |
| Frederickson Power 1 | CCCT | 280 | 0.059 |  |
| Fredonia 1 | GT | 111 | 0.051 |  |
| Fredonia 2 | GT | 111 | 0.051 |  |
| Fredonia 3 | GTAero | 59 | 0.051 |  |
| Fredonia 4 | GTAero | 59 | 0.051 |  |
| Freres Lumber (Evergreen Andrews Power Complex) | STCG | 10 | 0.07 |  |
| Galesville | Hyd | 0 | 0 |  |
| Geo-Bon No. 2 | Hyd | 0 | 0 |  |
| Georgia-Pacific (Camas) | STCG | 52 | 0.07 |  |
| Georgia-Pacific (Wauna) | STCG | 32 | 0.07 |  |
| Glenns Ferry Cogeneration | CCCT | 10 | 0.059 |  |
| Goldendale CC 1A & 1B | CCCT | 289 | 0.059 |  |
| Grant Village 1 & 2 | IC | 1 | 0.047 |  |
| Grays Harbor Energy Facility (Satsop) | CCCT | 0 | 0.059 | 650 |
| Ground Water Pumping Station | Hyd | 5 | 0 |  |
| H.W. Hill (Roosevelt Biogas) 1 - 5 | IC | 11 | 0.047 |  |
| Hampton Lumber | STCG | 4 | 0.07 |  |
| Hardin Generating Station | Coal | 0 | 0.067 | 109 |
| Hauser 1 - 6 | Hyd | 0 | 0 |  |
| Hazelton A | Hyd | 3 | 0 |  |
| Hazelton B | Hyd | 3 | 0 |  |
| Hermiston Generating Project CC 1A & 1B | CCCT | 236 | 0.059 |  |
| Hermiston Generating Project CC 2A & 2B | CCCT | 236 | 0.059 |  |
| Hermiston Power Project | CCCT | 0 | 0.059 | 630 |
| Hidden Hollow | Hyd | 3 | 0 |  |
| Holter 1 - 4 | Hyd | 0 | 0 |  |
| Horseshoe Bend Hydroelectric | Hyd | 4 | 0 |  |
| Ingram Warm Springs Ranch A | Hyd | 0 | 0 |  |
| Ingram Warm Springs Ranch B | Hyd | 0 | 0 |  |
| International Paper (Springfield) 4 | STCG | 22 | 0.07 |  |
| Iron Gate | Hyd | 18 | 0 |  |
| Jim Bridger 1 | Coal | 530 | 0.067 |  |
| Jim Bridger 2 | Coal | 530 | 0.067 |  |
| Jim Bridger 3 | Coal | 530 | 0.067 |  |
| Jim Bridger 4 | Coal | 530 | 0.067 |  |
| Jim Ford Creek 1-3 (Ford Hydro LP) | Hyd | 1 | 0 |  |
| John Day Creek (Cereghino) | Hyd | 0 | 0 |  |
| Juniper Ridge | Hyd | 3 | 0 |  |
| Kasel-Witherspoon | Hyd | 0 | 0 |  |
| Kettle Falls Generating Station | Biomass ST | 47 | 0.07 |  |
| Kettle Falls GT | GT | 11 | 0.051 |  |
| Name | Type | NW | FOR | IPP |
| Klamath Cogeneration Project | CCCT | 0 | 0.059 | 484 |
| Klamath Generation Peakers 1 & 2 | GTAero | 0 | 0.051 | 50 |
| Klamath Generation Peakers 3 & 4 | GTAero | 0 | 0.051 | 50 |
| Koma Kulshan | Hyd | 12 | 0 |  |
| Koyle Ranch 1-3 | Hyd | 0 | 0 |  |
| Lacomb | Hyd | 0 | 0 |  |
| Lake | IC | 0 | 0.047 |  |
| Lake Oswego | Hyd | 1 | 0 |  |
| Lancaster (Rathdrum Generating Station) | CCCT | 279 | 0.059 |  |
| Langley Gulch | CCCT | 300 | 0.059 |  |
| Lateral No. 10 | Hyd | 1 | 0 |  |
| Lilliwaup Falls 1 - 7 | Hyd | 0 | 0 |  |
| Little Mac (Cedar Draw) | Hyd | 2 | 0 |  |
| Little Wood Reservoir | Hyd | 0 | 0 |  |
| Little Wood River Ranch | Hyd | 0 | 0 |  |
| LM Angus Ranch | Hyd | 0 | 0 |  |
| Low Line Canal Drop (South Forks Hydro) | Hyd | 5 | 0 |  |
| Low Line Midway | Hyd | 1 | 0 |  |
| Lower Low Line (aka Low Line Rapids) | Hyd | 2 | 0 |  |
| LQ-LS Drains | Hyd | 2 | 0 |  |
| Lucky Peak 1 - 3 | Hyd | 0 | 0 |  |
| MacClaren | IC | 1 | 0.047 |  |
| Madison 1 - 4 | Hyd | 0 | 0 |  |
| Magic Dam | Hyd | 0 | 0 |  |
| Main Canal Headworks | Hyd | 0 | 0 |  |
| March Point 1 - 4 | CCCT | 145 | 0.059 |  |
| Marion Investment | Hyd | 0 | 0 |  |
| Marsh Valley | Hyd | 0 | 0 |  |
| Metro West Point Treatment Plant 1 - 3 | IC | 5 | 0.047 |  |
| Meyers Falls | Hyd | 1 | 0 |  |
| Middle Fork Irrigation District 1 | Hyd | 3 | 0 |  |
| Middle Fork Irrigation District 2 | Hyd | 0 | 0 |  |
| Middle Fork Irrigation District 3 | Hyd | 0 | 0 |  |
| Mile 28 (1 & 2) | Hyd | 1 | 0 |  |
| Mill Creek (Cove) 1 & 2 | Hyd | 0 | 0 |  |
| Mill Creek/Dave Gates Generating Station | IC | 47 | 0.047 |  |
| Mink Creek | Hyd | 0 | 0 |  |
| Mint Farm | CCCT | 301 | 0.059 |  |
| Mirror Lake (Hutchinson Creek) | Hyd | 1 | 0 |  |
| Mitchell Butte | Hyd | 0 | 0 |  |
| Montana One (Colstrip Energy) | Coal | 5 | 0.067 |  |
| Mora Canal Drop | Hyd | 2 | 0 |  |
| Morony 1 & 2 | Hyd | 0 | 0 |  |
| Morrow Power | GTAero | 0 | 0.051 | 25 |
| Mystic 1 & 2 | Hyd | 0 | 0 |  |
| Name | Type | NW | FOR | IPP |
| N-32 (Northside Canal) | Hyd | 0 | 0 |  |
| Nichols Gap | Hyd | 0 | 0 |  |
| North Fork Sprague River | Hyd | 0 | 0 |  |
| North Valmy 1 | Coal | 127 | 0.067 |  |
| North Valmy 2 | Coal | 134 | 0.067 |  |
| Northeast 1 | GTAero | 33 | 0.051 |  |
| Northeast 2 | GTAero | 33 | 0.051 |  |
| Old Faithful 1 & 2 | IC | 1 | 0.047 |  |
| Olympic View 1 & 2 | IC | 6 | 0.047 |  |
| Opal Springs | Hyd | 3 | 0 |  |
| Orchard Avenue 1 & 2 | Hyd | 0 | 0 |  |
| Owyhee Dam | Hyd | 0 | 0 |  |
| Owyhee Tunnel No. 1 | Hyd | 3 | 0 |  |
| Pasco (Franklin/Grays) GT 1 | GT | 11 | 0.051 |  |
| Pasco (Franklin/Grays) GT 2 | GT | 11 | 0.051 |  |
| Pasco (Franklin/Grays) GT 3 | GT | 11 | 0.051 |  |
| Pasco (Franklin/Grays) GT 4 | GT | 11 | 0.051 |  |
| Plummer Forest Products | STCG | 6 | 0.07 |  |
| Port Westward CC 1A & 1B | CCCT | 423 | 0.059 |  |
| Portland General Electric Distributed PV | PV | 11 | 0 |  |
| Portneuf River | Hyd | 0 | 0 |  |
| Potholes East Canal 66.0 | Hyd | 1 | 0 |  |
| Potholes East Canal Headworks | Hyd | 0 | 0 |  |
| Prather Creek | Hyd | 0 | 0 |  |
| Qualco | IC | 0 | 0.047 |  |
| Quincy Chute | Hyd | 0 | 0 |  |
| Raft River I | Geothermal | 13 | 0.021 |  |
| Rainbow 1 - 8 | Hyd | 0 | 0 |  |
| Rathdrum (Boekel Rd) 1 | GT | 88 | 0.051 |  |
| Rathdrum (Boekel Rd) 2 | GT | 88 | 0.051 |  |
| River Road Generating Plant | CCCT | 235 | 0.059 |  |
| Riverbend Landfill | IC | 5 | 0.047 |  |
| Rock Creek #1 | Hyd | 1 | 0 |  |
| Rock Creek #2 | Hyd | 1 | 0 |  |
| Rocky Brook | Hyd | 2 | 0 |  |
| Ross Creek | Hyd | 0 | 0 |  |
| Rough & Ready Lumber | STCG | 1 | 0.07 |  |
| Rupert Cogeneration | CCCT | 8 | 0.059 |  |
| Russell D. Smith | Hyd | 0 | 0 |  |
| Ryan 1 - 6 | Hyd | 0 | 0 |  |
| Sahko | Hyd | 1 | 0 |  |
| Salmon 1 | IC | 3 | 0.047 |  |
| Salmon 2 | IC | 3 | 0.047 |  |
| Savage Rapids Diversion | Hyd | 1 | 0 |  |
| Schaffner | Hyd | 0 | 0 |  |
| Name | Type | NW | FOR | IPP |
| Shasta River | Hyd | 0 | 0 |  |
| Short Mountain 1 - 4 | IC | 3 | 0.047 |  |
| Shoshone/Shoshone II | Hyd | 0 | 0 |  |
| Simpson Tacoma Kraft Cogeneration | STCG | 0 | 0.07 |  |
| Skookumchuck | Hyd | 1 | 0 |  |
| Slate Creek | Hyd | 4 | 0 |  |
| South Dry Creek | Hyd | 0 | 0 |  |
| SPI Aberdeen | STCG | 5 | 0.07 |  |
| SPI Burlington | STCG | 3 | 0.07 |  |
| Spokane Waste-to-Energy (Wheelabrator) | MSW | 15 | 0.07 |  |
| St. Anthony | Hyd | 1 | 0 |  |
| Stahlbush Island Farms | IC | 2 | 0.047 |  |
| Sumas Cogeneration Station | CCCT | 134 | 0.059 |  |
| Summer Falls 1 & 2 | Hyd | 0 | 0 |  |
| Tenaska Washington Partners Cogeneration Station | CCCT | 0 | 0.059 | 245 |
| Tiber-Montana | Hyd | 0 | 0 |  |
| Tieton Dam | Hyd | 0 | 0 |  |
| Tuttle Ranch (Ravenscroft) | Hyd | 1 | 0 |  |
| Twin Falls (TFHA) | Hyd | 20 | 0 |  |
| Twin Reservoirs | Hyd | 2 | 0 |  |
| U.S. Bankcorp IC1 - IC4 | IC | 6 | 0.047 |  |
| U.S. Navy (Puget Sound Naval Shipyard) | IC | 12 | 0.047 |  |
| U.S. Navy (Submarine Base Bangor) 1 | IC | 8 | 0.047 |  |
| U.S. Navy (Submarine Base Bangor) 2 | IC | 10 | 0.047 |  |
| Upriver | Hyd | 16 | 0 |  |
| Wapato Drop 2 (#1) | Hyd | 3 | 0 |  |
| Wapato Drop 3 (#1 - 2) | Hyd | 2 | 0 |  |
| Warm Springs Forest Products 1 - 3 | STCG | 0 | 0.07 |  |
| Weeks Falls | Hyd | 5 | 0 |  |
| Whitehorn Generating Station 2 | GT | 80 | 0.051 |  |
| Whitehorn Generating Station 3 | GT | 80 | 0.051 |  |
| Wild Horse Solar | PV | 0 | 0 |  |
| Wilson Lake | Hyd | 0 | 0 |  |
| Woods Creek 1 & 2 | Hyd | 1 | 0 |  |
| WSU Grimes Way Central Steam Plant | IC | 3 | 0.047 |  |
| Yellowstone Energy (BGI) | STCG | 7 | 0.07 |  |
| Youngs Creek | Hyd | 7 | 0 |  |
| Total |  | 12765 |  | 3451 |
| New since 2015 |  |  |  |  |
| Biotech/Life Sciences Building Generator 836 | IC | 1 | 0.047 |  |
| Black Cap Solar Project | PV | 2 | 0 |  |
| Burton Creek | Hyd | 0 | 0 |  |
| Esquatzel Power | Hyd | 1 | 0 |  |
| Fargo Drop | Hyd | 1 | 0 |  |
| Name | Type | NW | FOR | IPP |
| Fighting Creek Landfill | IC | 3 | 0.047 |  |
| H.W. Hill (Roosevelt Biogas) Expansion | IC | 26 | 0.047 |  |
| Highwood Generating Station I | GTAero | 13 | 0.051 |  |
| McKenzie | Hyd | 0 | 0 |  |
| Ponderosa | Hyd | 1 | 0 |  |
| Puyallup Energy Recovery Company (PERC) 1 - 3 (South Hill) | IC | 2 | 0.047 |  |
| Seneca Saw Mill | STCG | 19 | 0.07 |  |
| Misc Hyd Resource Lump * | Hyd | 29 | 0 |  |
| Misc Thr Resource Lump * | STCG | 15 | 0 |  |
| Total New |  | 114 |  |  |
| Total All |  | 12879 |  |  |

Table 10 - Wind Serving NW Loads

| Source Name | Cap | Owner | NW MW |
| --- | --- | --- | --- |
| Bennett Creek | 21 |  |  |
| Big Horn I | 199 | MSR | 0 |
| Big Horn II | 50 | MSR | 0 |
| Big Top (Echo Wind Farm) | 1.65 |  |  |
| Biglow Canyon I | 125.4 | PGE | 125.4 |
| Biglow Canyon II | 149.5 | PGE | 149.5 |
| Biglow Canyon III | 174.8 | PGE | 174.8 |
| Burley Butte | 19.5 | IDA | 19.5 |
| Butter Creek (Echo Wind Farm) | 4.95 | PAC | 4.95 |
| Camp Reed | 22.5 | IDA | 22.5 |
| Cassia | 10.5 | IDA | 10.5 |
| Cassia Gulch | 18.9 | IDA | 18.9 |
| Coastal Energy | 6 | Grays Harbor | 6 |
| Combine Hills I | 41 | PAC | 41 |
| Combine Hills II | 63 | Clark | 63 |
| Condon | 49.8 | BPA | 49.8 |
| Elkhorn Valley | 100 | IDA | 100 |
| Fairfield Wind |  |  |  |
| Foote Creek I | 41.4 | BPA, PAC, EWEB | 41.4 |
| Foote Creek II | 1.8 | BPA | 1.8 |
| Foote Creek IV | 16.8 | BPA | 16.8 |
| Fossil Gulch | 10.5 | IDA | 10.5 |
| Four Corners (Echo Wind Farm) | 10 | PAC | 10 |
| Four Mile Canyon (Echo Wind Farm) | 10 | PAC | 10 |
| Glacier Wind Energy I | 106.5 | N W E | 106.5 |
| Glacier Wind Energy II | 103.5 | N W E | 103.5 |
| Golden Valley | 12 | IDA | 12 |
| Goodnoe Hills | 94 | PAC | 94 |
| Gordon Butte |  |  |  |
| Goshen North (Goshen II) | 124.5 | SCE | 0 |
| Harvest Wind | 98.9 | WA Publics | 98.9 |
| Hay Canyon | 100.8 | Snohomish | 100.8 |
| Hopkins Ridge | 156.6 | PSE | 156.6 |
| Horse Butte | 57.6 | UAMP | 0 |
| Horseshoe Bend Wind Park | 10 | IDA | 9 |
| Hot Springs | 21 | IDA | 9 |
| Judith Gap | 135 | N W E | 135 |
| Juniper Canyon I | 151.2 | IPP | 151.2 |
| Kittitas Valley Wind | 100.8 | IPP | 100.8 |
| Klondike I | 24 | BPA | 24 |
| Klondike II | 75 | PGE | 75 |
| Klondike III | 223.6 | BPA, EWEB, PSE | 125 |
| Klondike IIIA | 76.5 | PG&E | 0 |
| Leaning Juniper I | 100.5 | PAC | 100.5 |
| Source Name | Cap | Owner | NW MW |
| Leaning Juniper IIa | 90.3 | IPP | 90.3 |
| Leaning Juniper IIb | 111 | IPP | 111 |
| Linden Ranch | 50 | SCPPA | 0 |
| Lower Snake River Phase I | 343 | PSE | 343 |
| Marengo I | 140.4 | PAC | 140.4 |
| Marengo II | 70.2 | PAC | 70.2 |
| Milner Dam | 19.5 | IDA | 19.5 |
| Musselshell Wind I |  |  |  |
| Musselshell Wind II |  |  |  |
| Nine Canyon | 95.9 | WA Publics | 95.9 |
| Oregon Trail (Echo Wind Farm) | 9.9 | PAC | 9.9 |
| Oregon Trail (Idaho Wind) | 13.5 | IDA | 13.5 |
| Pacific Canyon (Echo Wind Farm) | 8.25 | PAC | 8.25 |
| Palouse Wind | 104.4 | Avista | 104.4 |
| PaTu | 9 | PGE | 9 |
| Payne's Ferry | 21 | IDA | 21 |
| Pebble Springs | 99 | LADWP | 0 |
| Pilgrim Stage Station | 10.5 | IDA | 10.5 |
| Rattlesnake Road (aka Arlington Wind Power Project) | 102.9 | PG&E | 0 |
| Rock River I | 50 | Rocky Mnt | 0 |
| Rockland | 79.2 | IDA | 79.2 |
| Salmon Falls | 21 | IDA | 21 |
| Sand Ranch (Echo Wind Farm) | 9.9 | PAC | 9.9 |
| Sawtooth Winds | 22.4 | IDA | 22.4 |
| Shepherds Flat North (North Hurlburt) | 265 | SCE | 0 |
| Spion Kop | 40 | N W E | 40 |
| Star Point | 98.7 | Modesto | 0 |
| Stateline | 300 | BPA NW Utilities | 300 |
| Thousand Springs | 12 | IDA | 12 |
| Three-mile Canyon | 9.9 | PAC | 9.9 |
| Tuana Gulch | 10.5 | IDA | 10.5 |
| Tuana Springs (Cassia Gulch Expansion) | 16.8 | IDA | 16.8 |
| Tuolumne (Windy Point; Windy Point/Windy Flats I) | 136.6 | Turlock | 0 |
| Two Dot Projects | 3.22 | N W E | 3.22 |
| Two Dot Projects II |  |  |  |
| Vansycle Wind Energy Center I | 25 | PGE | 25 |
| Vansycle Wind Energy Center II | 98.9 | IPP | 98.9 |
| Vantage Wind Project | 90 | PG&E | 0 |
| Wagon Trail (Echo Wind Farm) | 3.3 | PAC | 3.3 |
| Ward Butte (Echo Wind Farm) | 6.6 | PAC | 6.6 |
| Wheat Field | 96.6 | Snohomish | 96.6 |
| White Creek | 204.7 | WA Publics | 204.7 |
| Wild Horse I & II | 272.6 | PSE | 272.6 |
| Willow Creek | 72 | LADWP | 0 |
| Windy Flats (Windy Point/Windy Flats IIA) | 262.2 | SCPPA | 0 |
| Source Name | Cap | Owner | NW MW |
| WKN |  |  |  |
| Wolverine Creek | 64.5 | Rocky Mnt | 0 |
| Yahoo Creek | 21 | IDA | 21 |
| Total |  |  | 4579 |

Table 11 - Average Monthly Load by Temperature Year

|  | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1929 | 23900 | 28072 | 31869 | 32063 | 28568 | 27253 | 26080 | 24003 | 24587 | 27872 | 25764 | 23340 |
| 1930 | 24412 | 29077 | 29140 | 35041 | 33812 | 26561 | 26829 | 23629 | 25138 | 26184 | 26224 | 23435 |
| 1931 | 24143 | 28110 | 31187 | 39369 | 28638 | 27913 | 24739 | 23440 | 24303 | 26403 | 26389 | 23442 |
| 1932 | 24024 | 32122 | 34092 | 29396 | 28501 | 27237 | 25440 | 23278 | 24156 | 26568 | 26437 | 23874 |
| 1933 | 24494 | 26702 | 37556 | 32917 | 33372 | 28269 | 25552 | 23350 | 25476 | 25643 | 25831 | 23814 |
| 1934 | 24037 | 28378 | 29382 | 32379 | 35040 | 27666 | 25417 | 23808 | 24710 | 26465 | 26192 | 23221 |
| 1935 | 23573 | 26773 | 29421 | 28578 | 27354 | 26336 | 24432 | 23265 | 24799 | 26201 | 25667 | 23721 |
| 1936 | 27951 | 29408 | 31026 | 40000 | 28635 | 27835 | 26482 | 23571 | 25425 | 27649 | 25152 | 23591 |
| 1937 | 24042 | 29259 | 31442 | 30812 | 33959 | 28991 | 27091 | 23077 | 25079 | 26601 | 25928 | 23396 |
| 1938 | 23577 | 27353 | 29869 | 39405 | 31042 | 26692 | 25281 | 23116 | 25444 | 26754 | 25380 | 23517 |
| 1939 | 23818 | 29342 | 31290 | 30536 | 28938 | 28033 | 24786 | 23865 | 25248 | 27160 | 24958 | 23605 |
| 1940 | 25035 | 26783 | 29676 | 28972 | 32167 | 28856 | 25622 | 23340 | 25396 | 27601 | 26273 | 23204 |
| 1941 | 24240 | 29203 | 32369 | 30288 | 27710 | 26381 | 25243 | 23161 | 25301 | 26734 | 26323 | 23598 |
| 1942 | 24045 | 28814 | 30717 | 32478 | 27754 | 26686 | 24479 | 23344 | 24700 | 28059 | 26376 | 23533 |
| 1943 | 24988 | 27680 | 30977 | 37001 | 29639 | 27713 | 24487 | 23846 | 25969 | 26559 | 25923 | 23641 |
| 1944 | 25077 | 26694 | 30682 | 39854 | 29126 | 28806 | 25033 | 23478 | 25418 | 26467 | 25904 | 23495 |
| 1945 | 23171 | 27688 | 31401 | 31027 | 28517 | 29027 | 25014 | 23550 | 25471 | 27198 | 25205 | 24191 |
| 1946 | 24243 | 28575 | 32607 | 29983 | 28270 | 28192 | 25855 | 23165 | 24986 | 26785 | 25707 | 23444 |
| 1947 | 25440 | 28825 | 31422 | 30620 | 28126 | 27256 | 25240 | 23088 | 24798 | 27145 | 25683 | 23415 |
| 1948 | 23492 | 28396 | 29647 | 33812 | 28412 | 27838 | 25469 | 23109 | 24192 | 26944 | 25629 | 23320 |
| 1949 | 24694 | 27684 | 33382 | 30526 | 29257 | 28069 | 25514 | 24152 | 26080 | 25814 | 25723 | 23469 |
| 1950 | 24925 | 26652 | 32834 | 38430 | 32162 | 27128 | 24339 | 23777 | 24053 | 26486 | 27537 | 23909 |
| 1951 | 24513 | 27379 | 29499 | 40522 | 40117 | 28452 | 25441 | 24370 | 25812 | 26388 | 26229 | 23784 |
| 1952 | 25330 | 28013 | 31682 | 34103 | 31541 | 30503 | 24817 | 23571 | 25806 | 26597 | 25893 | 23561 |
| 1953 | 24000 | 31403 | 30114 | 37931 | 29976 | 28430 | 25238 | 23719 | 24064 | 26498 | 26751 | 23232 |
| 1954 | 24136 | 26587 | 29139 | 29109 | 28360 | 28465 | 25957 | 23928 | 24232 | 26800 | 25195 | 23828 |
| 1955 | 24983 | 29165 | 31775 | 35420 | 28624 | 28970 | 25449 | 23837 | 24640 | 25986 | 25797 | 23076 |
| 1956 | 25207 | 33973 | 32371 | 30971 | 29996 | 30723 | 25948 | 23939 | 24678 | 26319 | 25433 | 24320 |
| 1957 | 25198 | 28816 | 35085 | 34316 | 34509 | 29379 | 25769 | 23494 | 25147 | 27587 | 25435 | 23453 |
| 1958 | 23920 | 28374 | 29227 | 37285 | 31491 | 27623 | 25297 | 23230 | 24907 | 25585 | 24777 | 23810 |
| 1959 | 23638 | 29167 | 29490 | 29383 | 27917 | 28414 | 25377 | 23136 | 25704 | 27675 | 26257 | 24013 |
| 1960 | 24054 | 30532 | 31270 | 40056 | 29024 | 28225 | 25041 | 24089 | 24996 | 27387 | 26024 | 23440 |
| 1961 | 23991 | 27894 | 30962 | 34432 | 30765 | 31183 | 24990 | 23476 | 25042 | 27199 | 27021 | 23253 |
| 1962 | 25020 | 28794 | 33762 | 32838 | 27446 | 28017 | 25771 | 23972 | 24904 | 27456 | 26914 | 23310 |
| 1963 | 23823 | 28768 | 30294 | 35306 | 31551 | 29354 | 24659 | 23676 | 25114 | 26875 | 25550 | 23805 |
| 1964 | 24517 | 28226 | 31375 | 39889 | 29820 | 27114 | 25174 | 23962 | 24719 | 25814 | 26362 | 23940 |
| 1965 | 24400 | 28466 | 34378 | 29577 | 29528 | 28325 | 25505 | 24437 | 24320 | 26480 | 25337 | 23154 |

|  | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1966 | 23368 | 27309 | 31755 | 30499 | 28957 | 27864 | 25715 | 24087 | 25309 | 27207 | 27438 | 23121 |
| 1967 | 23946 | 27085 | 30236 | 30992 | 28560 | 28587 | 25075 | 23249 | 24995 | 26050 | 26305 | 24015 |
| 1968 | 24101 | 27497 | 32983 | 29709 | 28461 | 27836 | 25285 | 23678 | 25208 | 26442 | 26472 | 24007 |
| 1969 | 24139 | 27137 | 37241 | 31541 | 27733 | 26827 | 25882 | 23554 | 24940 | 27019 | 26949 | 23906 |
| 1970 | 24291 | 29233 | 29844 | 35725 | 29818 | 27782 | 24988 | 24117 | 24451 | 26076 | 25351 | 23617 |
| 1971 | 25402 | 30664 | 31287 | 32455 | 27597 | 27959 | 25610 | 23651 | 25379 | 26863 | 25596 | 22943 |
| 1972 | 25970 | 26957 | 31774 | 33793 | 30783 | 30688 | 25888 | 23415 | 24979 | 27520 | 27135 | 23249 |
| 1973 | 25459 | 27243 | 36587 | 34786 | 32697 | 28080 | 25783 | 23415 | 25268 | 26134 | 27439 | 23425 |
| 1974 | 24343 | 27725 | 29062 | 35509 | 27985 | 27348 | 25710 | 23402 | 25659 | 26922 | 26061 | 24202 |
| 1975 | 23934 | 27732 | 30664 | 38416 | 28238 | 29272 | 25521 | 23638 | 25442 | 26595 | 26935 | 23617 |
| 1976 | 24609 | 32060 | 31177 | 33517 | 29948 | 27448 | 27177 | 23840 | 24315 | 27163 | 25487 | 23789 |
| 1977 | 23792 | 29041 | 30188 | 30628 | 29668 | 29726 | 25462 | 23175 | 25648 | 26437 | 25560 | 23431 |
| 1978 | 24206 | 31275 | 30995 | 34224 | 27818 | 28042 | 25020 | 23648 | 24872 | 26059 | 26919 | 23459 |
| 1979 | 25061 | 29643 | 38111 | 32152 | 27797 | 27434 | 25243 | 23751 | 25531 | 26958 | 27220 | 23110 |
| 1980 | 24220 | 29138 | 30156 | 35678 | 33414 | 27650 | 25249 | 23308 | 25146 | 27566 | 25920 | 23636 |
| 1981 | 24379 | 27391 | 32762 | 33526 | 30181 | 27468 | 25795 | 23327 | 24300 | 26539 | 25839 | 23662 |
| 1982 | 23572 | 28200 | 30606 | 28874 | 29926 | 26736 | 26052 | 23668 | 25015 | 26972 | 27303 | 23952 |
| 1983 | 24274 | 29375 | 31700 | 35067 | 30611 | 26836 | 26331 | 23716 | 25192 | 26449 | 26153 | 23532 |
| 1984 | 23848 | 28159 | 35956 | 30274 | 27939 | 26039 | 26005 | 23774 | 24806 | 25853 | 26261 | 23147 |
| 1985 | 26471 | 27702 | 36755 | 32686 | 28035 | 26374 | 25324 | 23787 | 25154 | 26756 | 26293 | 23306 |
| 1986 | 24840 | 35810 | 33158 | 32950 | 32022 | 28033 | 25495 | 23639 | 24726 | 27163 | 25283 | 23270 |
| 1987 | 23612 | 28178 | 30227 | 29608 | 29573 | 26508 | 25686 | 23516 | 25634 | 26023 | 26741 | 23865 |
| 1988 | 23655 | 28339 | 32459 | 32264 | 27960 | 26555 | 25358 | 23872 | 26427 | 26406 | 26817 | 24206 |
| 1989 | 24404 | 27815 | 31098 | 33289 | 30768 | 26986 | 25873 | 24391 | 25007 | 27415 | 25930 | 23619 |
| 1990 | 24511 | 27442 | 30769 | 31274 | 36718 | 31291 | 25491 | 23204 | 24623 | 26446 | 26026 | 23295 |
| 1991 | 24074 | 27253 | 39460 | 29572 | 32068 | 27106 | 24655 | 23103 | 25584 | 27190 | 26439 | 23960 |
| 1992 | 25782 | 28644 | 30122 | 33494 | 26767 | 27587 | 25593 | 23816 | 24505 | 26188 | 26510 | 24044 |
| 1993 | 23521 | 28977 | 33145 | 29563 | 27789 | 25714 | 25533 | 23412 | 26027 | 27463 | 26254 | 23275 |
| 1994 | 23828 | 32461 | 30943 | 34297 | 30499 | 28279 | 25324 | 23317 | 24662 | 24963 | 26804 | 23659 |
| 1995 | 24018 | 29475 | 32783 | 29147 | 30934 | 27386 | 24976 | 23333 | 24904 | 27628 | 26550 | 23534 |
| 1996 | 25174 | 26171 | 32249 | 30909 | 32096 | 27573 | 24964 | 23306 | 26046 | 27483 | 26062 | 23633 |
| 1997 | 24761 | 29138 | 30982 | 35236 | 33989 | 27196 | 25053 | 23940 | 24536 | 27461 | 25778 | 23339 |
| 1998 | 24367 | 26751 | 30612 | 31385 | 29502 | 27901 | 26292 | 23667 | 24340 | 26385 | 26547 | 23529 |
| 1999 | 24462 | 27126 | 38364 | 34213 | 27638 | 27729 | 24929 | 23321 | 25327 | 28139 | 26632 | 24098 |
| 2000 | 24074 | 26994 | 30206 | 30408 | 28761 | 27864 | 26708 | 24112 | 24505 | 26789 | 26184 | 23449 |
| 2001 | 24255 | 29080 | 32218 | 29986 | 27980 | 27428 | 24915 | 23382 | 25807 | 26242 | 26680 | 23352 |
| 2002 | 24151 | 27550 | 30251 | 31220 | 29898 | 27585 | 26040 | 23879 | 24937 | 26291 | 26366 | 23511 |
| 2003 | 26027 | 27360 | 30724 | 30289 | 28471 | 30056 | 24646 | 23658 | 25416 | 27137 | 25408 | 23562 |
| 2004 | 25705 | 30542 | 30292 | 28567 | 28545 | 27213 | 26164 | 23490 | 26114 | 27393 | 26333 | 24267 |
| 2005 | 24613 | 28862 | 29213 | 39682 | 28300 | 26619 | 24267 | 23109 | 25494 | 27774 | 26453 | 23606 |
| Average | 24458 | 28593 | 31838 | 33143 | 29949 | 27929 | 25454 | 23596 | 25078 | 26773 | 26151 | 23589 |

Table 12 - Maximum Hour Load by Temperature Year

|  | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1929 | 20031 | 22065 | 25076 | 24949 | 23697 | 21584 | 20562 | 19775 | 20619 | 21632 | 20931 | 19699 |
| 1930 | 19907 | 22764 | 23828 | 26779 | 25815 | 21965 | 20942 | 19875 | 20604 | 21301 | 21188 | 19771 |
| 1931 | 20280 | 22556 | 24953 | 28697 | 23102 | 21791 | 19873 | 19894 | 20516 | 21336 | 21303 | 19821 |
| 1932 | 20022 | 23067 | 25158 | 23952 | 23386 | 21869 | 20173 | 19754 | 20544 | 21563 | 21080 | 19798 |
| 1933 | 20056 | 21652 | 26114 | 25263 | 24394 | 22088 | 20248 | 19801 | 20846 | 20992 | 20993 | 19765 |
| 1934 | 19926 | 22054 | 23517 | 24778 | 25228 | 22158 | 20487 | 20035 | 20649 | 21307 | 21122 | 19681 |
| 1935 | 19900 | 21412 | 24097 | 23447 | 22660 | 20968 | 19543 | 19768 | 20679 | 21294 | 21160 | 19801 |
| 1936 | 20456 | 23096 | 24570 | 25059 | 23336 | 22682 | 20691 | 19885 | 20587 | 21261 | 20864 | 19889 |
| 1937 | 19920 | 22815 | 24158 | 24066 | 26189 | 22562 | 20090 | 19766 | 20846 | 21425 | 21210 | 19672 |
| 1938 | 19724 | 21679 | 24031 | 29045 | 24251 | 21687 | 20600 | 19781 | 20671 | 21441 | 20788 | 19869 |
| 1939 | 19919 | 22721 | 24276 | 24498 | 23588 | 22150 | 20125 | 19929 | 20811 | 21710 | 20739 | 19853 |
| 1940 | 19989 | 21844 | 23524 | 23860 | 24394 | 22234 | 20410 | 19797 | 20489 | 21421 | 21268 | 19710 |
| 1941 | 19790 | 22891 | 24160 | 24321 | 23039 | 21375 | 20064 | 19766 | 20901 | 21468 | 21165 | 19864 |
| 1942 | 20010 | 21864 | 24055 | 24297 | 22847 | 21138 | 19902 | 19836 | 20566 | 21826 | 21025 | 19637 |
| 1943 | 20045 | 22417 | 24108 | 26348 | 23844 | 22211 | 20136 | 19942 | 20451 | 21540 | 21247 | 19778 |
| 1944 | 20085 | 22080 | 24673 | 26587 | 23464 | 22595 | 20038 | 19968 | 20479 | 21275 | 20862 | 19830 |
| 1945 | 19661 | 22291 | 25043 | 24813 | 23641 | 22502 | 20390 | 19839 | 20559 | 21365 | 20880 | 19849 |
| 1946 | 20014 | 22231 | 24764 | 24148 | 23317 | 22392 | 20768 | 19750 | 20506 | 21498 | 21071 | 19735 |
| 1947 | 20462 | 22760 | 24214 | 24499 | 23401 | 22084 | 20403 | 19759 | 20461 | 21371 | 20990 | 19746 |
| 1948 | 19943 | 22385 | 24047 | 25844 | 23081 | 21634 | 20082 | 19701 | 20510 | 21350 | 20744 | 19687 |
| 1949 | 20182 | 22667 | 25648 | 24505 | 23712 | 22556 | 20653 | 19993 | 20769 | 20938 | 20640 | 19780 |
| 1950 | 20382 | 21402 | 24735 | 28797 | 24742 | 22067 | 20112 | 19760 | 20505 | 21150 | 20999 | 19831 |
| 1951 | 20155 | 22307 | 23519 | 29513 | 24517 | 22678 | 20758 | 20000 | 20631 | 21271 | 21109 | 19856 |
| 1952 | 20301 | 22427 | 25525 | 25299 | 23852 | 23294 | 20140 | 19819 | 20752 | 21439 | 20902 | 19791 |
| 1953 | 19768 | 23177 | 24265 | 26191 | 23992 | 22681 | 20285 | 19888 | 20376 | 21343 | 21061 | 19721 |
| 1954 | 19943 | 21676 | 23956 | 23328 | 23579 | 22305 | 20738 | 19877 | 20238 | 21171 | 20935 | 19878 |
| 1955 | 20215 | 21510 | 24532 | 25398 | 23480 | 22830 | 20781 | 19793 | 20344 | 20902 | 20503 | 19709 |
| 1956 | 20128 | 23201 | 24944 | 25042 | 24438 | 23511 | 21207 | 19960 | 20526 | 20784 | 20843 | 19841 |
| 1957 | 20371 | 22796 | 24789 | 24741 | 25479 | 22838 | 20247 | 19874 | 20411 | 21513 | 20846 | 19748 |
| 1958 | 20165 | 22492 | 23846 | 27421 | 24177 | 22212 | 20290 | 19747 | 20585 | 21056 | 20696 | 19856 |
| 1959 | 19904 | 22496 | 23733 | 23929 | 22402 | 22258 | 20447 | 19750 | 20871 | 21895 | 21487 | 19792 |
| 1960 | 20071 | 22785 | 24576 | 24891 | 23832 | 22176 | 20289 | 19970 | 20643 | 21592 | 20764 | 19682 |
| 1961 | 20007 | 22252 | 24896 | 25947 | 23757 | 22488 | 20430 | 19904 | 20637 | 21889 | 20737 | 19707 |
| 1962 | 20287 | 22952 | 24921 | 24054 | 22896 | 22010 | 20672 | 19951 | 20977 | 21709 | 21640 | 19712 |
| 1963 | 19969 | 21940 | 23931 | 25766 | 23644 | 22643 | 20165 | 19964 | 20701 | 21192 | 20744 | 19761 |
| 1964 | 19935 | 22060 | 24704 | 26769 | 22468 | 22127 | 20607 | 19927 | 20566 | 20971 | 21079 | 19924 |
| 1965 | 19985 | 22875 | 24971 | 24574 | 23895 | 22495 | 20762 | 20020 | 20427 | 21121 | 20692 | 19628 |
| 1966 | 19723 | 21587 | 24770 | 24654 | 23469 | 22088 | 20351 | 19993 | 20572 | 21609 | 21169 | 19633 |
| 1967 | 20130 | 22002 | 23823 | 24528 | 23411 | 22154 | 20231 | 19738 | 20570 | 21132 | 21090 | 19832 |
| 1968 | 19960 | 21964 | 24681 | 23893 | 23229 | 22574 | 20885 | 19879 | 20857 | 21658 | 21818 | 19924 |
| 1969 | 20069 | 21979 | 25244 | 24790 | 22446 | 21477 | 20730 | 19851 | 20674 | 21645 | 20818 | 19773 |
| 1970 | 20157 | 22104 | 24117 | 26897 | 23947 | 21994 | 20397 | 19786 | 20764 | 21244 | 20923 | 19786 |
| 1971 | 20333 | 22088 | 24793 | 24751 | 22664 | 22041 | 20948 | 19862 | 20840 | 21530 | 21135 | 19574 |
| 1972 | 20455 | 22183 | 25062 | 24817 | 23515 | 22831 | 20494 | 19760 | 20383 | 21514 | 21630 | 19684 |
|  | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep |
| 1973 | 20249 | 21919 | 25150 | 25674 | 23872 | 21730 | 20912 | 19813 | 20619 | 21461 | 21376 | 19747 |
| 1974 | 19998 | 22485 | 23801 | 25406 | 23169 | 22056 | 20405 | 19786 | 20685 | 21539 | 20846 | 19815 |
| 1975 | 20009 | 22101 | 24177 | 26193 | 23395 | 22066 | 20369 | 19917 | 20929 | 21246 | 21005 | 19885 |
| 1976 | 20205 | 22506 | 24345 | 25224 | 24265 | 22669 | 21082 | 19913 | 20454 | 21693 | 20689 | 19811 |
| 1977 | 20020 | 21966 | 24533 | 24403 | 23819 | 22915 | 20570 | 19731 | 20535 | 21352 | 20745 | 19756 |
| 1978 | 20012 | 22660 | 24615 | 25735 | 22781 | 22214 | 19948 | 19899 | 20894 | 21209 | 21545 | 19745 |
| 1979 | 20034 | 23283 | 26105 | 24264 | 22982 | 21414 | 20405 | 19892 | 20781 | 21434 | 21005 | 19639 |
| 1980 | 19931 | 22817 | 24016 | 26898 | 24002 | 21479 | 20394 | 19824 | 20736 | 21652 | 21070 | 19835 |
| 1981 | 20090 | 22113 | 24177 | 26267 | 23388 | 22277 | 20047 | 19757 | 20409 | 21301 | 20659 | 19718 |
| 1982 | 20138 | 21773 | 24369 | 23752 | 23350 | 21555 | 20503 | 19960 | 20427 | 21042 | 21502 | 19865 |
| 1983 | 20082 | 22848 | 24797 | 25265 | 23830 | 22185 | 20855 | 19910 | 20930 | 21047 | 21084 | 19796 |
| 1984 | 19989 | 21819 | 26139 | 23684 | 22696 | 21371 | 20367 | 19942 | 20541 | 20963 | 21279 | 19693 |
| 1985 | 20539 | 22342 | 26021 | 24415 | 23235 | 21544 | 20649 | 19975 | 20502 | 21344 | 21176 | 19746 |
| 1986 | 20204 | 25029 | 26543 | 25981 | 24678 | 22630 | 20288 | 19889 | 20669 | 21975 | 20855 | 19596 |
| 1987 | 19870 | 22222 | 24798 | 23960 | 23540 | 21280 | 20584 | 20016 | 20897 | 20760 | 21551 | 19757 |
| 1988 | 19862 | 21800 | 25160 | 24916 | 22936 | 21549 | 19990 | 19681 | 20921 | 21102 | 21036 | 19858 |
| 1989 | 19785 | 22179 | 24682 | 25196 | 23278 | 22029 | 20238 | 19893 | 20706 | 21394 | 21034 | 19835 |
| 1990 | 20097 | 21966 | 24590 | 24706 | 25604 | 22480 | 19900 | 19749 | 20771 | 21265 | 20838 | 19774 |
| 1991 | 20136 | 21933 | 26546 | 24038 | 24160 | 21701 | 19931 | 19850 | 20715 | 21704 | 21312 | 19898 |
| 1992 | 20292 | 22157 | 24185 | 25148 | 22415 | 22360 | 20515 | 19875 | 20388 | 21505 | 21301 | 19818 |
| 1993 | 19886 | 22410 | 25414 | 23962 | 22519 | 21036 | 20013 | 19735 | 21062 | 21457 | 21307 | 19654 |
| 1994 | 19887 | 23395 | 24580 | 26066 | 24225 | 21817 | 20359 | 19789 | 20542 | 20454 | 20926 | 19822 |
| 1995 | 20097 | 23028 | 24544 | 23618 | 24124 | 21524 | 20045 | 19725 | 20666 | 21802 | 21290 | 19790 |
| 1996 | 20185 | 21486 | 24475 | 23813 | 22862 | 21783 | 20333 | 19839 | 20706 | 21483 | 20712 | 19897 |
| 1997 | 20306 | 22551 | 24823 | 24960 | 23987 | 21983 | 20212 | 19970 | 20545 | 21703 | 21116 | 19685 |
| 1998 | 20130 | 21656 | 24668 | 24649 | 23622 | 22124 | 20569 | 19763 | 20536 | 21259 | 21458 | 19830 |
| 1999 | 20084 | 21738 | 25282 | 24388 | 23029 | 21819 | 20358 | 19751 | 20607 | 21950 | 21413 | 19982 |
| 2000 | 20021 | 21521 | 24102 | 24136 | 23452 | 22216 | 20654 | 20088 | 20552 | 21394 | 21196 | 19780 |
| 2001 | 19993 | 23220 | 24934 | 24713 | 23325 | 22188 | 19991 | 19866 | 20783 | 21367 | 21135 | 19683 |
| 2002 | 20192 | 21786 | 24517 | 24538 | 24119 | 22057 | 20669 | 19877 | 20577 | 21214 | 21257 | 19805 |
| 2003 | 20232 | 21977 | 24253 | 24499 | 23625 | 22842 | 20446 | 20009 | 20797 | 21620 | 20972 | 19783 |
| 2004 | 19786 | 22877 | 24224 | 23559 | 23502 | 21769 | 20446 | 19968 | 20877 | 21973 | 21404 | 19853 |
| 2005 | 19978 | 22179 | 24119 | 25477 | 23307 | 21334 | 19814 | 19718 | 20926 | 21926 | 21495 | 19729 |
| Average | 20066 | 22329 | 24637 | 25133 | 23653 | 22104 | 20390 | 19858 | 20644 | 21393 | 21071 | 19776 |

# Appendix C – Assuring Adequacy for a Resource Plan

The Resource Adequacy Forum has developed a method to assess the adequacy of the Northwest’s power supply.  More specifically, it has defined a probabilistic measure to gauge whether Northwest’s resources will sufficiently satisfy the region’s needs.  It focuses only on the adequacy of electricity supply and does not take transmission outages into account (it does capture variation in transmission capacity for the east-to-west regional interties).

The Northwest Resource Adequacy Standard uses the probabilistic measure defined by the Forum to assess whether existing resources will be sufficient through the next five year period.  That assessment only takes into account existing resources and new resources that are expected to be completed and operational during that time period.  If the power supply is deemed to be inadequate (e.g. LOLP greater than five percent), then specific actions are initiated.  Those actions include reporting the known problem, validating load and resource data and identifying potential solutions.

The process described above is intended to be an early warning for the region that indicates when resource development does not sufficiently keep up with demand.  Although similar, the assessment of a resource strategy differs in significant ways.  First, a resource strategy spans a much longer time period, namely 20 years for the Council’s power plan.  Second, a strategy implies that resource development will be dynamic, in other words, it does not identify specific resources and specific build dates.  Rather, the strategy identifies a supply of cost-effective resources that can be acquired as future conditions warrant.  One can extract a single resource plan out of a particular resource strategy and then assess the adequacy of that single plan but that is not the same as assessing the adequacy of the strategy itself.

The adequacy measure, as adopted by the Council, assesses the sufficiency of a specific set of resources combined with a specific forecasted demand by simulating the operation of those resources over many different futures.  In those futures, water conditions, temperatures (which affect load), wind generation and thermal resource availability can vary.  Based on those random variables only, a loss of load probability is calculated and compared to the five percent maximum allowed under the standard.

The five percent LOLP threshold can be translated into deterministic metrics, which are more easily used for assessing adequacy or for incorporation into resource planning models.  For example, a power system will provide an adequate supply of energy for the region when the average generation of existing resources plus about 1,500 average megawatts of market supply equals the average annual load.  Similarly, the system will provide an adequate supply of peaking capability when the surplus sustained-peak generating capability is 23 percent in winter and 24 percent in summer.  In each of these cases, the resulting LOLP will be five percent.

These calibrated deterministic metric thresholds are easily incorporated into the Council’s Resource Portfolio Model (RPM).  That model simulates a wider variety of future conditions with many more future unknowns than the Genesys model, which is used to assess LOLP.  The RPM acquires resources based on economic considerations but if those resources do not measure up to the deterministic adequacy metric threshold, the model will add resources until that condition is satisfied.  In this way, the Council can be sure that each resource plan examined under any particular resource strategy will be adequate, at least for energy supply.

The problem is that currently, the only adequacy metric incorporated into the RPM is the energy measure.  It may be possible (but unlikely) that some resource plans generated by the RPM may not meet the peaking adequacy thresholds.  Given that the region is transitioning from a winter energy-limited system into a summer capacity-limited system, this omission from the RPM needs to be addressed.  Perhaps future versions of the model can also include measures to test the peaking adequacy of various resource plans.

However, the question at hand is how to assess the adequacy of a resource strategy developed by the RPM.  One suggestion is to assess the adequacy of each resource plan (types of resources and build dates) for all 750 simulated futures for each strategy, using the deterministic adequacy metrics.  This is time consuming but very doable. However, it is not clear what an acceptable result would be.  Do all 750 plans need to be adequate or would it be acceptable if only 95 percent of them were adequate?  Another option would be to assess the adequacy of the “average” build-out schedule of the strategy.  If this average scenario is adequate does that imply that the strategy is adequate?

The problem is that the RPM simulates future conditions with many more random variables than does Genesys.  The most important variable, from an adequacy point of view, is probably long-term load uncertainty.  This is not the uncertainty in demand caused by variation in temperature but rather the potentially much larger change in demand due to economic or other factors.  A result of this is that the RPM will simulate situations when the region will under or overbuild, much like it has in real life over the past 50 years.  There really is no way to avoid such conditions because we cannot accurately forecast all future conditions, especially demand.  We could have the RPM calculate a loss of load probability for its all of its plans in each strategy but that calculation could be misleading.  Although labeled LOLP, the RPM version provides a vastly different measure of the power supply than does the Genesys LOLP because the random variables are different.  At this time it is unknown what a reasonable RPM LOLP value would be or whether it would ever be meaningful, since the RPM is not an hourly simulation model and thus can only approximate peaking operations.

So what do we do?

The first thing to remember is that the real scope of this power plan has a five year time period.  We will revisit these questions five years from now. So, potential inadequacies in the later years of the study horizon may be interesting but are unlikely to change the five-year action plan.  Thus, if we are to assess the adequacy of all (or some) of the resource build-outs from an RPM strategy, we should only focus on the first five years.  It seems to me that most of those plans should pass the Genesys adequacy test (at least the deterministic ones).  If a significant number of those plans fail the test, we should ask ourselves why that is and perhaps change our five-year action plan to address the problem.  However, this does not appear to be the case for the draft power plan.

There is the additional issue of whether the adequacy of all RPM strategies should be assessed.  Some of those strategies are based on assumptions that have little or no likelihood of being realized.  In those cases, it makes no sense to spend the time calculating adequacy, especially because they do not drive the action items in the plan.   Thus the current recommendation is to simply use some form of deterministic adequacy metric inside of the RPM to dynamically test for adequacy during the analysis.  It is not recommended that we take any of the “build-out” cases out of the RPM and assess the LOLP specifically.

________________________________________

q:\jf\2017 adequacy\sos\2017 sos report draft 4.docx